## Main Data
Standard Data - Electrical Items For Buildings
Index-code | Specification No. | Description | Unit | Quantity | Rate Rs. | Amount Rs. | Remarks
| 1 | 2 | 3 | 4 | 5 | 6 | 7
BLD-ELEC-1 |  | Conduit Laying
BLD-ELEC-1 | 1 | MS / PVC / Trunks Coduit Laying
BLD-ELEC-1-1 | 1.1 | M.S.CONDUIT (Surface)
| 1.1.1 | Supply and Fixing of 20mm dia 16 SWG (ISI Mark) MS Surface conduit pipe duly threading at Joints with all required accessories fixing on T.W. Separators with chromium plated base saddles and No.18 SWG MS box for light, fan and separate plug points including cost of Cement, all materials, accessories and all labour charges etc., complete. |  |  |  |  | Note for All Items for Coduit Laying
Taking Output = 100 M
a) Material
|  | 20mm dia 16 SWG MS conduit | 100 M | 1
|  | T.W seperators | 100 Nos | 2
|  | 30mm Screws No.8 | 100 Nos | 2
|  | Rawal Plugs | 100 Nos | 2
|  | 12mm Screws | 100 Nos | 4
|  | 20mm Saddles MS | 100 Nos | 2
|  | 20mm 1,2,3 & 4 way Junction box | Dozen | 1
|  | 20mm dia HG bends | Dozen | 1
|  | 200mm x 250mm sheet metal deep box | Each | 3
|  | Cement (As per civil SSR) | kg | 12.5
b) Labour charges :
|  | Skilled Electrician | day | 3
|  | Semi skilled Electrician | day | 3
|  | Helpers | day | 3
Sundries
C) Cost for 100 RM
Rate per Metre = C/100
| 1.1.2 | Supply and Fixing of 25mm dia 16 SWG (ISI MARK) MS Surface pipe duly threading at Joints with all required accessories fixing on T.W. Seperators with chromium plated base saddles and No.18 SWG MS box for run of mains including cost of Cement, all materials, accessories and all labour charges etc., complete.
Taking Output = 100 M
a) Material
|  | 25mm dia 16 SWG MS conduit | 100 M | 1
|  | T.W seperators | 100 Nos | 1.5
|  | 38mm Screws No.8 | 100 Nos | 1.5
|  | Rawal Plugs | 100 Nos | 1.5
|  | 12mm Screws | 100 Nos | 3
|  | 25mm Saddles MS | 100 Nos | 1.5
|  | 25mm 1,2,3 & 4 way Junction box | Dozen | 0.5
|  | 25mm dia HG bends | Dozen | 1
|  | Cement (As per civil SSR) | kg | 12.5
b) Labour charges :
|  | Skilled Electrician | day | 3
|  | Semi skilled Electrician | day | 3
|  | Helpers | day | 3
Sundries
C) Cost for 100 RM
Rate per Metre = C/100
| 1.1.3 | Supply and Fixing of 32mm dia 16 SWG (ISI MARK) MS Surface pipe duly threading at Joints with all required accessories fixing on T.W. Seperators with chromium plated base saddles and No.18 SWG MS box for run of mains including cost of Cement, all materials, accessories and all labour charges etc., complete.
Unit = 1Metre
Taking Output = 100 M
a) Material
|  | 32mm dia 16 SWG MS conduit | 100 M | 1
|  | T.W seperators | 100 Nos | 1.5
|  | 38mm Screws No.8 | 100 Nos | 1.5
|  | Rawal Plugs | 100 Nos | 1.5
|  | 12mm Screws | 100 Nos | 3
|  | 32mm Saddles MS | 100 Nos | 1.5
|  | 32mm 1,2,3 & 4 way Junction box | Dozen | 0.5
|  | 32mm dia HG bends | Dozen | 1
|  | Cement (As per civil SSR) | kg | 12.5
b) Labour charges :
|  | Skilled Electrician | day | 3
|  | Semi skilled Electrician | day | 3
|  | Helpers | day | 3
Sundries
C) Cost for 100 RM
Rate per Metre = C/100
BLD-ELEC-1-2 | 1.2 | MS Conduit Concealed
| 1.2.1 | Supply and Fixing of 20mm dia 16 SWG (ISI Mark) MS concealed conduit, duly threadig at Joints, on wall with required accessories including chiselling the wall for light, Fan and separate plug point including necessary sheet metal deep boxes, masonsary work and all labour charges etc. complete.
Taking Output = 100 M
a) Material
|  | 20mm dia 16 SWG MS conduit pipe | 100 M | 1
|  | U' Nails | 100 Nos | 2
|  | 200mm x 250mm sheet metal deep box | Each | 3
|  | 20mm HG bends | Dozen | 1
|  | Cement | kg | 12.5
b) Labour charges :
|  | Skilled Electrician | day | 3
|  | Semi skilled Electrician | day | 3
|  | Helpers | day | 3
|  | Mason Ist class | day | 3
Sundries
C) Cost for 100 RM
Rate per Metre = C/100
| 1.2.2 | Supply and Fixing of 25mm dia 16 SWG (ISI MARK) MS concealed conduit, duly threadig at Joints in Slab and on wall with required accessories including chiselling the wall and necessary Masonary and all labour charges etc. complete for run of mains.
Taking Output = 100 M
a) Material
|  | 25mm dia 16 SWG MS conduit pipe | 100 M | 1
|  | U' Nails | 100 Nos | 2
|  | 25 mm Deep Junction Box | Dozen | 1
|  | 25mm HG bends | Dozen | 1
|  | Cement | kg | 50
b) Labour charges :
|  | Skilled Electrician | day | 3
|  | Semi skilled Electrician | day | 3
|  | Helpers | day | 3
|  | Mason Ist class | day | 3
Sundries
C) Cost for 100 RM
Rate per Metre = C/100
| 1.2.3 | Supply and Fixing of 32mm dia 16 SWG (ISI Mark) MS concealed conduit, duly threadig at Joints in Slab and on wall with required accessories including chiselling the wall and necessary Masonary and all labour charges etc. complete for run of mains.
Taking Output = 100 M
a) Material
|  | 32mm dia 16 SWG MS conduit pipe | 100 M | 1
|  | U' Nails | 100 Nos | 2
|  | 32 mm Deep Junction Box | Dozen | 1
|  | 32mm HG bends | Dozen | 1
|  | Cement | kg | 50
b) Labour charges :
|  | Skilled Electrician | day | 3
|  | Semi skilled Electrician | day | 3
|  | Helpers | day | 3
|  | Mason Ist class | day | 3
Sundries
C) Cost for 100 RM
Rate per Metre = C/100
NOTE : For Laying MS Concealed Conduit pipe in roof Slab, deduct the Cost of Cement and U' Nails.
BLD-ELEC-1-3 | 1.3 | P.V.C. Conduit (Surface)
| 1.3.1 | Supply and Fixing of 20mm dia 1.5mm thick surface P.V.C. pipe (ISI MARK) with all accessories fixing on chromium plated metallic base saddles and decolam board for switches for Light, Fan and separate plug point including all labour charges etc., complete.
Taking Output = 100 M
a) Material
|  | 20mm dia 1.5mm thick PVC pipe | 100 M | 1
|  | Rawl Plugs | 100 Nos | 2
|  | 35mm Screws | 100 Nos | 2
|  | Chromium Plated saddles with base | Each | 200
|  | 20mm 1,2,3, & 4 way Junction boxes | Each | 12
|  | 20mm PVC Bends | Each | 12
|  | 8" x10" Decolam Board | Each | 3
|  | Cement | kg | 25
b) Labour charges :
|  | Skilled Electrician | day | 2
|  | Semi skilled Electrician | day | 2
|  | Helpers | day | 2
Sundries
C) Cost for 100 RM
Rate per Metre = C/100
| 1.3.2 | Supply and Fixing of 25mm dia 1.5mm thick surface P.V.C. pipe (ISI MARK) with all accessories fixing on chromium plated metallic base saddles including all labour charges etc., complete for run of mains.
Taking Output = 100 M
a) Material
|  | 25mm dia 1.5mm thick PVC pipe | 100 M | 1
|  | Rawl Plugs | 100 Nos | 2
|  | 35mm Screws | 100 Nos | 2
|  | Chromium Plated saddles with base | Each | 200
|  | 25mm 1,2,3, & 4 way Junction boxes | Each | 12
|  | 25mm PVC Bends | Each | 12
|  | Cement | kg | 25
b) Labour charges :
|  | Skilled Electrician | day | 2
|  | Semi skilled Electrician | day | 2
|  | Helpers | day | 2
Sundries
C) Cost for 100 RM
Rate per Metre = C/100
| 1.3.3 | Supply and Fixing of 32mm dia 2mm thick surface P.V.C. pipe (ISI Mark) with all accessories fixing on chromium plated metallic base saddles including all labour charges etc., complete for run of mains
Taking Output = 100 M
a) Material
|  | 32mm dia 1.5mm thick PVC pipe | 100 M | 1
|  | Rawl Plugs | 100 Nos | 2
|  | 35mm Screws | 100 Nos | 2
|  | Chromium Plated saddles with base | Each | 200
|  | 32mm 1,2,3, & 4 way Junction boxes | Each | 12
|  | 32mm PVC Bends | Each | 12
|  | Cement | kg | 25
b) Labour charges :
|  | Skilled Electrician | day | 2
|  | Semi skilled Electrician | day | 2
|  | Helpers | day | 2
Sundries
C) Cost for 100 RM
Rate per Metre = C/100
| 1.3.4 | Supply and Fixing of 40mm dia 2mm thick surface P.V.C. pipe (ISI MARK) with all accessories fixing on chromium plated metallic base saddles including all labour charges etc., complete for run of mains.
Taking Output = 100 M
a) Material
|  | 40mm dia 1.5mm thick PVC pipe | 100 M | 1
|  | Rawl Plugs | 100 Nos | 2
|  | 35mm Screws | 100 Nos | 2
|  | Chromium Plated saddles with base | Each | 200
|  | 40mm 1,2,3, & 4 way Junction boxes | Each | 12
|  | 40mm PVC Bends | Each | 12
|  | Cement | kg | 25
b) Labour charges :
|  | Skilled Electrician | day | 2
|  | Semi skilled Electrician | day | 2
|  | Helpers | day | 2
Sundries
C) Cost for 100 RM
Rate per Metre = C/100
| 1.3.5 | Supply and Fixing of 50mm dia 2mm thick surface P.V.C. pipe (ISI MARK) with all accessories fixing on chromium plated metallic base saddles including all labour charges etc., complete for run of mains.
Taking Output = 100 M
a) Material
|  | 50mm dia 1.5mm thick PVC pipe | 100 M | 1
|  | Rawl Plugs | 100 Nos | 2
|  | 35mm Screws | 100 Nos | 2
|  | Chromium Plated saddles with base | Each | 200
|  | 50mm 1,2,3, & 4 way Junction boxes | Each | 12
|  | 50mm PVC Bends | Each | 12
|  | Cement | kg | 25
b) Labour charges :
|  | Skilled Electrician | day | 2
|  | Semi skilled Electrician | day | 2
|  | Helpers | day | 2
Sundries
C) Cost for 100 RM
Rate per Metre = C/100
BLD-ELEC-1-4 | 1.4 | P.V.C. Conduit (Concealed)
| 1.4.1 (a) | Supply and Fixing of 20mm dia 2mm thick P.V.C. pipe (ISI MARK) concealed in wall with all required accessories including masonary work for light, fan and separate plug point with well seasoned wooden deep box including all labour charges etc., complete.
Taking Output = 100 M
a) Material
|  | 20mm dia 2mm thick PVC pipe | 100 M | 1
|  | U' Links | 100 Nos | 2
|  | 10" x 8" Wooden deep box | Each | 3
|  | 20mm dia 1,2,3 & 4 way deep Junction Box | Each | 12
|  | 20mm PVC bends | Each | 12
|  | Cement | kg | 50
b) Labour charges :
|  | Skilled Electrician | day | 2
|  | Semi skilled Electrician | day | 2
|  | Helpers | day | 2
|  | Mason Ist class | day | 2
Sundries
C) Cost for 100 RM
Rate per Metre = C/100
| (b) | Supply and Fixing of 20mm dia 1.5mm thick P.V.C. pipe (ISI MARK) concealed in wall with all required accessories including masonary work for light, fan and separate plug point with well seasoned wooden deep box including all labour charges etc., complete.
Taking Output = 100 M
a) Material
|  | 20mm dia 1.5mm thick PVC pipe | 100 M | 1
|  | U' Links | 100 Nos | 2
|  | 10" x 8" Wooden deep box | Each | 3
|  | 20mm dia 1,2,3 & 4 way deep Junction Box | Each | 12
|  | 20mm PVC bends | Each | 12
|  | Cement | kg | 50
b) Labour charges :
|  | Skilled Electrician | day | 2
|  | Semi skilled Electrician | day | 2
|  | Helpers | day | 2
|  | Mason Ist class | day | 2
Sundries
C) Cost for 100 RM
Rate per Metre = C/100
| 1.4.2 (a) | Supply and Fixing of 25mm dia 2mm thick PVC pipe (ISI MARK) concealed in wall with all required accessories including masonary work and labour charges etc., complete.
Taking Output = 100 M
a) Material
|  | 25mm dia 2mm thick PVC pipe | 100 M | 1
|  | U' Links | 100 Nos | 2
|  | 25mm dia 1,2,3 & 4 way deep Junction Box | Each | 12
|  | 25mm PVC bends | Each | 12
|  | Cement | kg | 50
b) Labour charges :
|  | Skilled Electrician | day | 2
|  | Semi skilled Electrician | day | 2
|  | Helpers | day | 2
|  | Mason Ist class | day | 2
Sundries
C) Cost for 100 RM
Rate per Metre = C/100
| (b) | Supply and Fixing of 25mm dia 1.5mm thick PVC pipe (ISI MARK) concealed in wall with all required accessories including masonary work and labour charges etc., complete.
Taking Output = 100 M
a) Material
|  | 25mm dia 1.5mm thick PVC pipe | 100 M | 1
|  | U' Links | 100 Nos | 2
|  | 25mm dia 1,2,3 & 4 way deep Junction Box | Each | 12
|  | 25mm PVC bends | Each | 12
|  | Cement | kg | 50
b) Labour charges :
|  | Skilled Electrician | day | 2
|  | Semi skilled Electrician | day | 2
|  | Helpers | day | 2
|  | Mason Ist class | day | 2
Sundries
C) Cost for 100 RM
Rate per Metre = C/100
Supply and Fixing of 25mm dia 2mm thick PVC pipe (ISI MARK) concealed in Roof Slabs with all required accessories including masonary work and labour charges etc., complete.
Taking Output = 100 M
a) Material
|  | 25mm dia 2mm thick PVC pipe | 100 M | 1
|  | 25mm dia 1,2,3 & 4 way deep Junction Box | Each | 12
|  | 25mm PVC bends | Each | 12
b) Labour charges :
|  | Skilled Electrician | day | 2
|  | Semi skilled Electrician | day | 2
|  | Helpers | day | 2
Sundries
C) Cost for 100 RM
Rate per Metre = C/100
Note : 1. If 25mm dia PVC / MS pipes are used for light / fan point, add the cost of sheet metal / well seasoned wooden board / box.
BLD-ELEC-1-5 | 1.5 | P.V.C. Casing and Caping
| 1.5.1 | Supply and Laying of P.V.C casing and caping (ISI MARK) with double locking arrangments with groover trunking of size not below 12.5mm height 19/20mm size with all accessories, duly sealed at points and erected on Wall / Ceiling including cost of all materials and labour charges complete.
Taking Output = 100 M
a) Material
|  | 19mm / 20mm x 12.5 mm height Casing and Caping | 100 M | 1
b) Labour charges :
|  | Skilled Electrician | day | 1
|  | Semi skilled Electrician | day | 1
|  | Helpers | day | 2
|  | Sundries such as screws, Rawal Plugs, Gutting, Cement, Sand and Rounding off. | LS
C) Cost for 100 RM
Rate per Metre = C/100
| 1.5.2 | Supply and Laying of P.V.C casing and caping (ISI MARK) with double locking arrangments with groover trunking of size not below 12.5mm height 25mm size with all accessories, duly sealed at points and erected on Wall / Ceiling including cost of all materials and labour charges complete.
Taking Output = 100 M
a) Material
|  | 25mm x 12.5 mm height Casing and Caping | 100 M | 1
b) Labour charges :
|  | Skilled Electrician | day | 1
|  | Semi skilled Electrician | day | 1
|  | Helpers | day | 2
|  | Sundries such as screws, Rawal Plugs, Gutting, Cement, Sand and Rounding off. | LS
C) Cost for 100 RM
Rate per Metre = C/100
| 1.5.3 | Supply and Laying of P.V.C casing and caping (ISI MARK) with double locking arrangments with groover trunking of size not below 12.5mm height 31/32mm size with all accessories, duly sealed at points and erected on Wall / Ceiling including cost of all materials and labour charges complete.
Taking Output = 100 M
a) Material
|  | 30 / 32mm x 12.5 mm height Casing and Caping | 100 M | 1
b) Labour charges :
|  | Skilled Electrician | day | 1
|  | Semi skilled Electrician | day | 1
|  | Helpers | day | 2
|  | Sundries such as screws, Rawal Plugs, Gutting, Cement, Sand and Rounding off. | LS
C) Cost for 100 RM
Rate per Metre = C/100
| 1.5.4 | Supply and Laying of P.V.C casing and caping (ISI MARK) with double locking arrangments with groover trunking of size not below 12.5mm height 38/40 size with all accessories, duly sealed at points and erected on Wall / Ceiling including cost of all materials and labour charges complete.
Taking Output = 100 M
a) Material
|  | 38 / 40mm x 12.5 mm height Casing and Caping | 100 M | 1
b) Labour charges :
|  | Skilled Electrician | day | 1
|  | Semi skilled Electrician | day | 1
|  | Helpers | day | 2
|  | Sundries such as screws, Rawal Plugs, Gutting, Cement, Sand and Rounding off. | LS
C) Cost for 100 RM
Rate per Metre = C/100
BLD-ELEC-2 | 2 | Wiring |  |  |  |  | Note for All Items for Wiring
BLD-ELEC-2-1 | 2.1 | Copper Wiring
| 2.1.1 | Wiring with 2 runs of 14/0.3mm (1.0 Sq.mm) Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A switch, Ceiling rose and 3mm thick hylam sheet covering to switch control box including all labour charges etc., complete for light, bell, fan and exhaust fan points in Non-Residential Buildings |  |  |  |  | The R&B Department Proposed Labour, for both piping & wiring considering 40% Labour, for Wire draw. Keeping this, the labour is proposed for wiring 100 RM.
Taking Output = 6 Points
a) Material
|  | 14/0.3mm PVC FR flexible copper wire | 100 M | 1
|  | 6A Switch @16/each | each | 6
|  | 6A 2 way Ceiling Rose@17/each | each | 6
|  | 25 x 20 cms (10" x8") Hylam sheet 3mm thick | sqm | 0.05
b) Labour charges :
|  | Skilled Electrician | day | 0.6
|  | Semi skilled Electrician | day | 1.2
|  | Helpers | day | 0.6
C) Cost for 6 Points
Rate per Point = C/6
| 2.1.2 | Wiring with 2 runs of 14/0.3mm (1.0 Sq.mm) P.V.C. insulated F.R flexible copper cable (ISI MARK) in existing pipe with 6A switch, Ceiling rose and 3mm thick hylam sheet covering to switch control box including all labour charges etc., complete for light, bell, fan and exhaust fan points in Residential Buildings.
Taking Output = 7 Points
a) Material
|  | 14/0.3mm PVC FR flexible copper wire | 100 M | 1
|  | 6A Switch @16/each | each | 7
|  | 6A 2 way Ceiling Rose@17/each | each | 7
|  | 25 x 20 cms (10" x8") Hylam sheet 3mm thick | sqm | 0.05
b) Labour charges :
|  | Skilled Electrician | day | 0.7
|  | Semi skilled Electrician | day | 1.4
|  | Helpers | day | 0.7
C) Cost for 7 Points
Rate per Points = C/7
| 2.1.3 | Wiring with 2 of 14/0.3mm (1.0 Sq.mm) P.V.C. insulated F.R. flexible copper cable (ISI MARK) in existing pipe with 6A switch control and 3/2 pin sockets fixing on separate board including all labour charges etc., complete.
Taking Output = 15 Points
a) Material
|  | 14/0.3mm PVC FR flexible copper wire | 100 M | 1
|  | 6A switches @16/each | each | 15
|  | 6A 3 pin / 2 Pin Socket | each | 15
b) Labour charges :
|  | Skilled Electrician | day | 1.5
|  | Semi skilled Electrician | day | 1.5
|  | Helpers | day | 1.5
C) Cost for 15 Points
Rate per Points = C/15
| 2.1.4 | Supply and fixing of 6A 3 pin wall plug socket with 6A switch control on a common switch board with earth continuity including wire leads, earth connections along with all labour charges etc., complete.
Taking Output = each
a) Material
|  | 6A 3 pin / 2 pin Socket | each | 1
|  | 6A switch | each | 1
b) Labour charges :
|  | Skilled Electrician | day | 0.067
|  | Helpers | day | 0.067
Rate per each
Note : Labour Charges proposed for 1point considering 15 per day
| 2.1.5 | Supply and fixing of 16A 3pin / 6A 3pin plug socket with indicator lamp and 16Amps fuse unit and 16 Amps switch control (5 in one) on decolam sheet covered board including earth connection and all labour charges etc., complete on wall.
Taking Output = each
a) Material
|  | 20 x 15 cms (8" x6") Decolam sheet covered board | each | 1
|  | 16A 3 pin / 6A 3pin Plug socket with indicator lamp, fuse unit (5 in 1) | each | 1
b) Labour charges :
|  | Skilled Electrician | day | 0.1
|  | Helpers | day | 0.1
Rate per each
Note : Labour Charges proposed for 1point considering 10 per day
| 2.1.6 | Supply and Fixing of 16A 3pin and 6A 3pin plug socket with indicator lamp and 16A fuse unit and 16A switch control (5 in 1) duly recessed in wall with wooden deep box of 6" x8" x2 1/2" size covered with hylam sheet including earth connections and all labour charges etc., complete.
Taking Output = each
a) Material
|  | 20 x 15 cms (8" x6") Wooden deep box | each | 1
|  | 21.6 x 16.6 cms (8.5 x 6.5") 3mm thick hylam sheet | each | 1
|  | 16A 3 pin / 6A 3pin plug socket (5 in 1) | each | 1
b) Labour charges :
|  | Skilled Electrician | day | 0.1
|  | Semi Skilled Electrician | day | 0.1
|  | Helpers | day | 0.1
Rate per each
Note : Labour Charges proposed for 10 jobs per day
| 2.1.7 | Supply and fixing of batten holder / slanting holder in lieu of ceiling rose of light point complete with all connections and all labour charges with 40W bulb (for new installation).
Taking Output = each
a) Material
|  | PVC batten holder | each | 1
|  | 40W bulb | each | 1
b) Labour charges :
|  | Skilled Electrician | day | 0.05
|  | Helpers | day | 0.05
Rate per each
Note : 1. The Cost of Ceiling Rose may be deducted in view of holder.
2. Labour Charges proposed for 20 jobs per day
| 2.1.8 | Supply and fixing of batten holder / angle holder on existing block, but without bulb including all connections etc., complete (For replacement).
Taking Output = each
a) Material
|  | PVC batten holder | each | 1
Less : Cost of ceiling Rose
b) Labour charges :
|  | Skilled Electrician | day | 0.05
|  | Helpers | day | 0.05
Rate per each
NOTE : Labour Charges proposed for 20 jobs per day
| 2.1.9 | Supply and fixing of 0.5mtr length angle iron upright of size 40mmx40mmx6mm with eye bolt and shackle insulator with accessories and all labour charges etc., complete.
Taking Output = each
a) Material
|  | 40x40x6mm angle iron | Kg | 5
|  | Eye bolt. | each | 1
|  | Shackle Insulator | each | 1
b) Labour charges :
|  | Semi Skilled Electrician | day | 0.125
|  | Mason 2nd class | day | 0.125
|  | Welder 2nd Class | day | 0.125
Rate per each
NOTE : Labour Charges proposed for 8 jobs per day
| 2.1.10 | Supply and fixing of bed light transformer with M.C. holders including giving connections and cost of all accessories and all labour charges etc., complete with bulb.
Taking Output = each
a) Material
|  | Bed light transformer | each | 1
|  | M.C.holder | each | 1
|  | 6V bulb | each | 1
b) Labour charges :
|  | Skilled Electrician | day | 0.05
|  | Helpers | day | 0.05
Rate per each
NOTE : Labour Charges proposed for 20 jobs per day
| 2.1.11 | Supply and fixing of night lamp fixed at 30 cms height from floor level with 100 x 178 x 20 mm (4"x7"x3/4") wooden deep box, acrylic cover and batten holder including cost of all accessories and labour charges etc., complete with bulb.
Taking Output = each
a) Material
|  | 100 x 178 (4"x7") wooden deep box | each | 1
|  | Acrylic cover | each | 1
|  | Batten holder | each | 1
|  | Zero watt bulb | each | 1
b) Labour charges :
|  | Skilled Electrician | day | 0.05
|  | Helpers | day | 0.05
Rate per each
NOTE : Labour Charges proposed for 20 jobs per day
| 2.1.12 | Supply and fixing of buzzer / Calling bell on 100 x 100 mm (4"x4") decolam block including giving connections, cost of all accessories and labour charges etc., complete.
Taking Output = each
a) Material
|  | Buzzer | each | 1
|  | 100 x 100 mm (4"x4") decolam block | each | 1
b) Labour charges :
|  | Skilled Electrician | day | 0.062
|  | Helpers | day | 0.062
Rate per each
NOTE : Labour Charges proposed for 16 jobs per day
| 2.1.13 | Supply and fixing of ding dong bell on 100 x 178 mm (4"x7") decolam block including giving connections cost of all accessories and all labour charges etc., complete.
Taking Output = each
a) Material
|  | Ding Dong bell | each | 1
|  | 100 x 178 mm (4"x7") Decolam block | each | 1
b) Labour charges :
|  | Skilled Electrician | day | 0.062
|  | Helpers | day | 0.062
Rate per each
NOTE : Labour Charges proposed for 16 jobs per day
| 2.1.14 | Supply and fixing of Electronic musical bell on 150 x 200 mm (6"x8") decolam block including giving connections cost of all accessories and all labour charges etc., complete.
Taking Output = each
a) Material
|  | Electronic Musical bell | Nos | 1
|  | 150 x 200 mm (6"x8") Decolam block | Nos | 1
b) Labour charges :
|  | Skilled Electrician | day | 0.062
|  | Helpers | day | 0.062
Rate per each
NOTE : Labour Charges proposed for 16 jobs per day
BLD-ELEC-3 | 3 | RUN OF MAINS
BLD-ELEC-3-1 | 3.1 | Wiring with F.R P.V.C. insulated flexible copper cable
| 3.1.1 | Supply and run of 2 of 14/0.3mm (1.0 Sq.mm) F.R P.V.C. insulated flexible copper cable in existing pipe for mains inlcuding all labour charges etc., complete.
Taking Output = 100 M
a) Material
|  | 14/0.3mm FR PVC copper wire | 100 M | 2
b) Labour charges :
|  | Skilled Electrician | day | 0.67
|  | Semi Skilled Electrician | day | 2
|  | Helpers | day | 0.67
Sundries
C) Cost for 100 RM
Rate per Metre = C/100
Note : Labour Charges considered for 150 M / day
| 3.1.2 | Supply and run of 1 of 14 /0.3mm (1.0 Sq.mm) FR P.V.C. insulated flexible copper cable in existing pipe for earth continuity including all labour charges etc., complete.
Taking Output = 100 M
a) Material
|  | 14/0.3mm FR PVC copper wire | 100 M | 1
b) Labour charges :
|  | Skilled Electrician | day | 0.34
|  | Semi Skilled Electrician | day | 1
|  | Helpers | day | 0.34
Sundries
C) Cost for 100 RM
Rate per Metre = C/100
Note : Labour Charges considered for 150 M / day
| 3.1.3 | Supply and run of 2 of 22/0.3mm (1.5 Sq.mm) F.R P.V.C. insulated flexible copper cable in existing pipe for mains inlcuding all labour charges etc., complete.
Taking Output = 100 M
a) Material
|  | 22/0.3mm FR PVC copper wire | 100 M | 2
b) Labour charges :
|  | Skilled Electrician | day | 0.67
|  | Semi Skilled Electrician | day | 2
|  | Helpers | day | 0.67
Sundries
C) Cost for 100 RM
Rate per Metre = C/100
Note : Labour Charges considered for 150 M / day
| 3.1.4 | Supply and run of 2 of 36/0.3mm (2.5 Sq.mm) F.R P.V.C. insulated flexible copper cable in existing pipe for mains inlcuding all labour charges etc., complete.
Taking Output = 100 M
a) Material
|  | 36/0.3mm (2.5 sqmm) FR PVC copper wire | 100 M | 2
b) Labour charges :
|  | Skilled Electrician | day | 0.67
|  | Semi Skilled Electrician | day | 2
|  | Helpers | day | 0.67
Sundries
C) Cost for 100 RM
Rate per Metre = C/100
Note : Labour Charges considered for 150 M / day
| 3.1.4 (a) | Supply and run of 1 of 36/0.3mm (2.5 Sq.mm) F.R P.V.C. insulated flexible copper cable in existing pipe for earth continuity inlcuding all labour charges etc., complete.
Taking Output = 100 M
a) Material
|  | 36/0.3mm (2.5 sqmm) FR PVC copper wire | 100 M | 1
b) Labour charges :
|  | Skilled Electrician | day | 0.34
|  | Semi Skilled Electrician | day | 1
|  | Helpers | day | 0.34
Sundries
C) Cost for 100 RM
Rate per Metre = C/100
Note : Labour Charges considered for 150 M / day
| 3.1.5 | Supply and run of 2 of 56/0.3mm (4 Sq.mm) FR P.V.C. insulated flexible copper cable in existing pipe for mains inlcuding all labour charges etc., complete.
Taking Output = 100 M
a) Material
|  | 56 /0.3mm (4 sqmm)FR PVC flexible copper wire. | 100 M | 2
b) Labour charges :
|  | Skilled Electrician | day | 1
|  | Semi Skilled Electrician | day | 3
|  | Helpers | day | 1
Sundries
C) Cost for 100 RM
Rate per Metre = C/100
Note : Labour Charges considered for 100 M / day
| 3.1.6 | Supply and run of 2 of 84/0.3mm (6.0 Sq.mm) FR P.V.C. insulated flexible copper cable in existing pipe for mains inlcuding all labour charges etc., complete.
Taking Output = 100 M
a) Material
|  | 84 /0.3mm (6 Sq.mm) FR PVC flexible copper wire. | 100 M | 2
b) Labour charges :
|  | Skilled Electrician | day | 1
|  | Semi Skilled Electrician | day | 3
|  | Helpers | day | 1
Sundries
C) Cost for 100 RM
Rate per Metre = C/100
Note : Labour Charges considered for 100 M / day
| 3.3.7 | Supply and run of 2 of 140 /0.3mm (10 Sq.mm) F.R PVC insulated flexible copper cable in existing pipe for mains including all labour charges etc., complete.
Taking Output = 100 M
a) Material
|  | 140/0.3 (10 Sq.mm) FR PVC flexible copper wire | 100 M | 2
b) Labour charges :
|  | Skilled Electrician | day | 1
|  | Semi Skilled Electrician | day | 3
|  | Helpers | day | 1
Sundries
C) Cost for 100 RM
Rate per Metre = C/100
Note : Labour Charges considered for 100 M / day
| 3.3.8 | Supply and run of 2 of 126 /0.4mm (16 Sq.mm) F.R PVC insulated flexible copper cable in existing pipe for mains including all labour charges etc., complete.
Taking Output = 100 M
a) Material
|  | 126/0.4mm (16 Sq.mm) FR PVC flexible copper wire | 100 M | 2
b) Labour charges :
|  | Skilled Electrician | day | 1
|  | Semi Skilled Electrician | day | 3
|  | Helpers | day | 1
Sundries
C) Cost for 100 RM
Rate per Metre = C/100
Note : Labour Charges considered for 100 M / day
BLD-ELEC-4 | 4 | SWITCH GEAR & MCB DISTRIBUTION BOARDS.
| 4.1 | Panel Mounting Cubical type SDF
| 4.1.1 | Supply and erection of Panel mounting cubical type 30 / 32A TPN 415V, 50 Hz. switch disconnector fuse unit complete with front drive mechanism with door inter lock, padlocking arrangement etc., complete with fuse links on existing control panel.
Taking Output = each
a) Material
|  | 30 / 32A TPN 415V, 50 Hz. switchs Disconnector fuse unit with HRC fuses. | each | 1
b) Labour charges :
|  | Skilled Electrician | day | 0.167
|  | Semi Skilled Electrician | day | 0.167
|  | Helpers | day | 0.333
|  | Sundries such as hardware etc., | LS
Rate per each
Note : Labour Charges considered for 6 jobs / day
| 4.1.2 | Supply and erection of Panel mounting cubical type 60 / 63A TPN 415V, 50 Hz. switch disconnector fuse unit complete with front drive mechanism with door inter lock, padlocking arrangement etc., complete with fuse links on existing control panel.
Taking Output = each
a) Material
|  | 60 / 63A TPN 415V, 50 Hz. switchs Disconnector fuse unit with HRC fuses. | each | 1
b) Labour charges :
|  | Skilled Electrician | day | 0.167
|  | Semi Skilled Electrician | day | 0.167
|  | Helpers | day | 0.333
|  | Sundries such as hardware etc., | LS
Rate per each
Note : Labour Charges considered for 6 jobs / day
| 4.1.3 | Supply and erection of Panel mounting cubical type 125A TPN 415V, 50 Hz. switch disconnector fuse unit complete with front drive mechanism with door inter lock, padlocking arrangement etc., complete with fuse links on existing control panel.
Taking Output = each
a) Material
|  | 125A TPN 415V, 50 Hz. switchs Disconnector fuse unit with HRC fuses. | each | 1
b) Labour charges :
|  | Skilled Electrician | day | 0.167
|  | Semi Skilled Electrician | day | 0.167
|  | Helpers | day | 0.333
|  | Sundries such as hardware etc., | LS
Rate per each
Note : Labour Charges considered for 6 jobs / day
| 4.1.4 | Supply and erection of Panel mounting cubical type 200A TPN 415V, 50 Hz. switch disconnector fuse unit complete with front drive mechanism with door inter lock, padlocking arrangement etc., complete with fuse links on existing control panel.
Taking Output = each
a) Material
|  | 200A TPN 415V, 50 Hz. switchs Disconnector fuse unit with HRC fuses. | each | 1
b) Labour charges :
|  | Skilled Electrician | day | 0.2
|  | Semi Skilled Electrician | day | 0.4
|  | Helpers | day | 0.4
|  | Sundries such as hardware etc., | LS
Rate per each
Note : Labour Charges considered for 5 jobs / day
| 4.1.5 | Supply and erection of Panel mounting cubical type 250A TPN 415V, 50 Hz. switch disconnector fuse unit complete with front drive mechanism with door inter lock, padlocking arrangement etc., complete with fuse links on existing control panel.
Taking Output = each
a) Material
|  | 250A TPN 415V, 50 Hz. switchs Disconnector fuse unit with HRC fuses. | each | 1
b) Labour charges :
|  | Skilled Electrician | day | 0.2
|  | Semi Skilled Electrician | day | 0.4
|  | Helpers | day | 0.4
|  | Sundries such as hardware etc., | LS
Rate per each
Note : Labour Charges considered for 5 jobs / day
| 4.1.6 | Supply and erection of Panel mounting cubical type 400A TPN 415V, 50 Hz. switch disconnector fuse unit complete with front drive mechanism with door inter lock, padlocking arrangement etc., complete with fuse links on existing control panel.
Taking Output = each
a) Material
|  | 400A TPN 415V, 50 Hz. switchs Disconnector fuse unit with HRC fuses. | each | 1
b) Labour charges :
|  | Skilled Electrician | day | 0.25
|  | Semi Skilled Electrician | day | 0.5
|  | Helpers | day | 0.5
|  | Sundries such as hardware etc., | LS
Rate per each
Note : Labour Charges considered for 4 jobs / day
| 4.1.7 | Supply and erection of Panel mounting cubical type 630A TPN 415V, 50 Hz. switch disconnector fuse unit complete with front drive mechanism with door inter lock, padlocking arrangement etc., complete with fuse links on existing control panel.
Taking Output = each
a) Material
|  | 630A TPN 415V, 50 Hz. switchs Disconnector fuse unit with HRC fuses. | each | 1
b) Labour charges :
|  | Skilled Electrician | day | 0.25
|  | Semi Skilled Electrician | day | 0.5
|  | Helpers | day | 0.5
|  | Sundries such as hardware etc., | LS
Rate per each
Note : Labour Charges considered for 4 jobs / day
BLD-ELEC-4-2 | 4.2 | Panel Mounting Cubical type, 4pole onload change over switch confirming to IS 13947-3-1993.
| 4.2.1 | Supply and erection of Panel mounting cubical type L.T heavy duty ON LOAD change over switch of 60 / 63A, 4 pole, 415V, 50 Hz. with all accessories etc., complete on existing control panel.
Taking Output = each
a) Material
|  | 60 / 63A, 4 Pole, 415V, 50 Hz. On load cubical type C.O.S | each | 1
b) Labour charges :
|  | Skilled Electrician | day | 0.167
|  | Semi Skilled Electrician | day | 0.167
|  | Helpers | day | 0.333
|  | Sundries such as hardware etc., | LS
Rate per each
Note : Labour Charges considered for 6 jobs / day
| 4.2.2 | Supply and erection of Panel mounting cubical type L.T heavy duty ON LOAD change over switch of 125A, 4 pole, 415V, 50 Hz. with all accessories etc., complete on existing control panel.
Taking Output = each
a) Material
|  | 125A, 4 Pole, 415V, 50 Hz. On load cubical type C.O.S | each | 1
b) Labour charges :
|  | Skilled Electrician | day | 0.167
|  | Semi Skilled Electrician | day | 0.167
|  | Helpers | day | 0.333
|  | Sundries such as hardware etc., | LS
Rate per each
Note : Labour Charges considered for 6 jobs / day
| 4.2.3 | Supply and erection of Panel mounting cubical type L.T heavy duty ON LOAD change over switch of 200A, 4 pole, 415V, 50 Hz. with all accessories etc., complete on existing control panel.
Taking Output = each
a) Material
|  | 200A, 4 Pole, 415V, 50 Hz. On load cubical type C.O.S | each | 1
b) Labour charges :
|  | Skilled Electrician | day | 0.2
|  | Semi Skilled Electrician | day | 0.4
|  | Helpers | day | 0.4
|  | Sundries such as hardware etc., | LS
Rate per each
Note : Labour Charges considered for 5 jobs / day
| 4.2.4 | Supply and erection of Panel mounting cubical type L.T heavy duty ON LOAD change over switch of 250A, 4 pole, 415V, 50 Hz. with all accessories etc., complete on existing control panel.
Taking Output = each
a) Material
|  | 250A, 4 Pole, 415V, 50 Hz. On load cubical type C.O.S | each | 1
b) Labour charges :
|  | Skilled Electrician | day | 0.2
|  | Semi Skilled Electrician | day | 0.4
|  | Helpers | day | 0.4
|  | Sundries such as hardware etc., | LS
Rate per each
Note : Labour Charges considered for 5 jobs / day
| 4.2.5 | Supply and erection of Panel mounting cubical type L.T heavy duty ON LOAD change over switch of 400A, 4 pole, 415V, 50 Hz. with all accessories etc., complete on existing control panel.
Taking Output = each
a) Material
|  | 400A, 4 Pole, 415V, 50 Hz. On load cubical type C.O.S | each | 1
b) Labour charges :
|  | Skilled Electrician | day | 0.25
|  | Semi Skilled Electrician | day | 0.5
|  | Helpers | day | 0.5
|  | Sundries such as hardware etc., | LS
Rate per each
Note : Labour Charges considered for 4 jobs / day
| 4.2.6 | Supply and erection of Panel mounting cubical type L.T heavy duty ON LOAD change over switch of 630A, 4 pole, 415V, 50 Hz. with all accessories etc., complete on existing control panel.
Taking Output = each
a) Material
|  | 630A, 4 Pole, 415V, 50 Hz. On load cubical type C.O.S | each | 1
b) Labour charges :
|  | Skilled Electrician | day | 0.25
|  | Semi Skilled Electrician | day | 0.5
|  | Helpers | day | 0.5
|  | Sundries such as hardware etc., | LS
Rate per each
Note : Labour Charges considered for 4 jobs / day
| 4.2.7 | Supply and erection of Panel mounting cubical type L.T heavy duty ON LOAD change over switch of 800A, 4 pole, 415V, 50 Hz. with all accessories etc., complete on existing control panel.
Taking Output = each
a) Material
|  | 800A, 4 Pole, 415V, 50 Hz. On load cubical type C.O.S | each | 1
b) Labour charges :
|  | Skilled Electrician | day | 1
|  | Semi Skilled Electrician | day | 1
|  | Helpers | day | 1
|  | Sundries such as hardware etc., | LS
Rate per each
| 4.2.8 | Supply and erection of Panel mounting cubical type L.T heavy duty ON LOAD change over switch of 1060A, 4 pole, 415V, 50 Hz. with all accessories etc., complete on existing control panel.
Taking Output = each
a) Material
|  | 1060A, 4 Pole, 415V, 50 Hz. On load cubical type C.O.S | each | 1
b) Labour charges :
|  | Skilled Electrician | day | 1
|  | Semi Skilled Electrician | day | 1
|  | Helpers | day | 1
|  | Sundries such as hardware etc., | LS
Rate per each
BLD-ELEC-4-3 | 4.3 | Panel Mounting Moulded Case Circute Breakers (MCCBs)
| 4.3.1 | Supply and erection of Panel mounting 60 / 63A, 3 Pole, 10 /16kA, MCCB with thermal magnetic setting / Microprocessor based release arrangement with all connections etc., complete on existing panel.
Taking Output = each
a) Material
|  | 60 / 63A, 3 Pole, 10 / 16kA, MCCB. | each | 1
b) Labour charges :
|  | Skilled Electrician | day | 0.167
|  | Semi Skilled Electrician | day | 0.167
|  | Helpers | day | 0.333
|  | Sundries such as hardware etc., | LS
Rate per each
Note : Labour Charges considered for 6 jobs / day
| 4.3.2 | Supply and erection of Panel mounting 60 / 63A, 4 Pole, 10 / 16kA, MCCB with thermal magnetic setting / Microprocessor based release arrangement with all connections etc., complete on existing panel.
Taking Output = each
a) Material
|  | Cost of 60 / 63A, 4 Pole Panel mounting 10 / 16 kA, MCCB | each | 1
b) Labour charges :
|  | Skilled Electrician | day | 0.167
|  | Semi Skilled Electrician | day | 0.167
|  | Helpers | day | 0.333
|  | Sundries such as hardware etc., | LS
Rate per each
Note : Labour Charges considered for 6 jobs / day
| 4.3.3 | Supply and erection of Panel mounting 125A, 3 Pole, 25kA, MCCB with thermal magnetic setting / Microprocessor based release arrangement with all connections etc., complete on existing panel.
Taking Output = each
a) Material
|  | Cost of 125A, 3 Pole, 25 kA panel mounting MCCB. | each | 1
b) Labour charges :
|  | Skilled Electrician | day | 0.167
|  | Semi Skilled Electrician | day | 0.167
|  | Helpers | day | 0.333
|  | Sundries such as hardware etc., | LS
Rate per each
Note : Labour Charges considered for 6 jobs / day
| 4.3.4 | Supply and erection of Panel mounting 125A, 4 Pole, 25kA, MCCB with thermal magnetic setting / Microprocessor based release arrangement with all connections etc., complete on existing panel.
Taking Output = each
a) Material
|  | Cost of 125A, 4 Pole, 25 kA panel mounting MCCB. | each | 1
b) Labour charges :
|  | Skilled Electrician | day | 0.167
|  | Semi Skilled Electrician | day | 0.167
|  | Helpers | day | 0.333
|  | Sundries such as hardware etc., | LS
Rate per each
Note : Labour Charges considered for 6 jobs / day
| 4.3.5 | Supply and erection of Panel mounting 250A, 4 Pole, 35 / 36kA, MCCB with thermal magnetic setting / Microprocessor based release arrangement with all connections etc., complete on existing panel.
Taking Output = each
a) Material
|  | 250A, 4 Pole, 36/35kA panel mounting MCCB | each | 1
b) Labour charges :
|  | Skilled Electrician | day | 0.2
|  | Semi Skilled Electrician | day | 0.4
|  | Helpers | day | 0.4
|  | Sundries such as hardware etc., | LS
Rate per each
Note : Labour Charges considered for 5 jobs / day
| 4.3.6 | Supply and erection of Panel mounting 400A, 4 Pole, 35 /36kA, MCCB with thermal magnetic setting / Microprocessor based release arrangement with all connections etc., complete on existing panel.
Taking Output = each
a) Material
|  | 400A, 4 Pole, 36/35kA panel mounting MCCB | each | 1
b) Labour charges :
|  | Skilled Electrician | day | 0.2
|  | Semi Skilled Electrician | day | 0.4
|  | Helpers | day | 0.4
|  | Sundries such as hardware etc., | LS
Rate per each
Note : Labour Charges considered for 5 jobs / day
BLD-ELEC-4-4 | 4.4 | DISTRIBUTION BOARDS
| 4.4.1 | Supply and fixing SPN Distribution board with IP-20 protection suitable for single phase Earth Leakage Circute Braker (ELCB) / Residual Current Circute Braker (RCCB) / Double Pole (DP) Isolator as incomer and 10kA SP MCBs as out going including internal connections and labour charges for surface / flush mounting etc., complete.
| A | 40A DP Isolator / RCCB / ELCB - 1 No for incomer, 6-32A SP MCBs - 4Nos for outgoing.
Taking Output = each
a) Material
|  | SPN 4way D.B with IP-20 Protection suitable for single phase ECCB / RCCB/ DP Isolator. | each | 1
|  | 40A D.P.Isolator / ECCB / RCCB | each | 1
|  | 10 kA - 6-32A range SP MCBs | each | 4
b) Labour charges :
|  | Skilled Electrician | day | 0.5
|  | Semi Skilled Electrician | day | 0.5
|  | Helpers | day | 1
|  | Sundries such as hardware, cement etc, | LS
Rate per each
Note : Labour Charges considered for 2 jobs / day
| B | 40A DP Isolator / RCCB / ELCB - 1 No for incomer, 6-32A SP MCBs - 6Nos for outgoing.
Taking Output = each
a) Material
|  | SPN 8way D.B with IP-20 Protection suitable for single phase ECCB / RCCB/ DP Isolator. | each | 1
|  | 40A D.P.Isolator / ECCB / RCCB | each | 1
|  | 10 kA - 6-32A range SP MCBs | each | 6
b) Labour charges :
|  | Skilled Electrician | day | 0.5
|  | Semi Skilled Electrician | day | 0.5
|  | Helpers | day | 1
|  | Sundries such as hardware, cement etc, | LS
Rate per each
Note : Labour Charges considered for 2 jobs / day
| C | 40A DP Isolator / RCCB / ELCB - 1 No for incomer, 6-32A SP MCBs - 8Nos for outgoing.
Taking Output = each
a) Material
|  | SPN 12 way D.B with IP-20 Protection suitable for single phase ECCB / RCCB/ DP Isolator. | each | 1
|  | 40A D.P.Isolator / ECCB / RCCB | each | 1
|  | 10 kA - 6-32A range SP MCBs | each | 8
b) Labour charges :
|  | Skilled Electrician | day | 0.5
|  | Semi Skilled Electrician | day | 0.5
|  | Helpers | day | 1
|  | Sundries such as hardware, cement etc, | LS
Rate per each
Note : Labour Charges considered for 2 jobs / day
| 4.4.2 | Supply and fixing SPN Distribution board with IP-42 protection (Metal Door) suitable for single phase ELCB / RCCB/DP Isolator as incomer and 10kA SP MCBs as outing going including internal connection and labour charges for surface / flush mounting etc., complete.
| A | 40A DP Isolator/ RCCB / ELCB - 1 No for incomer, 6-32A SP MCBs - 4Nos for outgoing.
Taking Output = each
a) Material
|  | SPN 4 way D.B with IP-42 Protection (MD) suitable for single phase ECCB / RCCB/ DP Isolator. | each | 1
|  | 40A D.P.Isolator / ECCB / RCCB | each | 1
|  | 10 kA - 6-32A range SP MCBs | each | 4
b) Labour charges :
|  | Skilled Electrician | day | 0.5
|  | Semi Skilled Electrician | day | 0.5
|  | Helpers | day | 1
|  | Sundries such as hardware, cement etc, | LS
Rate per each
Note : Labour Charges considered for 2 jobs / day
| B | 40A DP Isolator / RCCB / ELCB - 1 No for incomer, 6-32A SP MCBs - 6Nos for outgoing.
Taking Output = each
a) Material
|  | SPN 8 way D.B with IP-42 Protection (MD) suitable for single phase ECCB / RCCB/ DP Isolator. | each | 1
|  | 40A D.P.Isolator / ECCB / RCCB | each | 1
|  | 10 kA - 6-32A range SP MCBs | each | 6
b) Labour charges :
|  | Skilled Electrician | day | 0.5
|  | Semi Skilled Electrician | day | 0.5
|  | Helpers | day | 1
|  | Sundries such as hardware, cement etc, | LS
Rate per each
Note : Labour Charges considered for 2 jobs / day
| C | 40A DP Isolator/ RCCB / ELCB - 1 No for incomer, 6-32A SP MCBs - 8 Nos for outgoing.
Taking Output = each
a) Material
|  | SPN 12 way D.B with IP-42 Protection (MD) suitable for single phase ECCB / RCCB/ DP Isolator. | each | 1
|  | 40A D.P.Isolator / ECCB / RCCB | each | 1
|  | 10 kA - 6-32A range SP MCBs | each | 8
b) Labour charges :
|  | Skilled Electrician | day | 0.5
|  | Semi Skilled Electrician | day | 0.5
|  | Helpers | day | 1
|  | Sundries such as hardware, cement etc, | LS
Rate per each
Note : Labour Charges considered for 2 jobs / day
| 4.4.3 | Supply and fixing TPN Distribution board with IP-20 protection suitable for 3 phase ELCB / RCCB / FP Isolator as incomer and 10kA SP MCBs as outing going including internal connection and labour charges for surface / flush mounting etc., complete.
| A | 40A FP Isolator/ RCCB / ELCB - 1 No for incomer, 10kA-6-32A SP MCBs - 12Nos for outgoing.
Taking Output = each
a) Material
|  | 4way TPN, D.B with IP-20 Protection suitable for 3 phase ELCB / RCCB/ FP Isolator as incommer. | each | 1
|  | 40A, 4 Pole Isolator / ELCB / RCCB | each | 1
|  | 10kA - 6-32A range SP MCBs | each | 12
b) Labour charges :
|  | Skilled Electrician | day | 0.5
|  | Semi Skilled Electrician | day | 1
|  | Helpers | day | 1
|  | Sundries such as TW Plugs, Screws Cement etc, | LS
Rate per each
Note : Labour Charges considered for 2 jobs / day
| B | 63A FP Isolator - 1 No for incomer, 10kA- 6-32A SP MCBs - 12Nos for outgoing.
Taking Output = each
a) Material
|  | 4way TPN, D.B with IP-20 Protection suitable for 3 phase ELCB / RCCB/ FP Isolator as incommer. | each | 1
|  | 63A, 4 Pole Isolator / ELCB / RCCB | each | 1
|  | 10kA - 6-32A range SP MCBs | each | 12
b) Labour charges :
|  | Skilled Electrician | day | 0.5
|  | Semi Skilled Electrician | day | 1
|  | Helpers | day | 1
|  | Sundries such as TW Plugs, Screws Cement etc, | LS
Rate per each
Note : Labour Charges considered for 2 jobs / day
| C | 80A FP Isolator - 1 No for incomer, 10kA- 6-32A SP MCBs - 18Nos for outgoing.
Taking Output = each
a) Material
|  | 6 way TPN, D.B with IP-20 Protection suitable for 3 phase ELCB / RCCB/ FP Isolator as incommer. | each | 1
|  | 80A, 4 Pole Isolator / ELCB / RCCB | each | 1
|  | 10kA - 6-32A range SP MCBs | each | 18
b) Labour charges :
|  | Skilled Electrician | day | 0.5
|  | Semi Skilled Electrician | day | 1
|  | Helpers | day | 1
|  | Sundries such as TW Plugs, Screws Cement etc, | LS
Rate per each
Note : Labour Charges considered for 2 jobs / day
| 4.4.4 | Supply and fixing TPN Distribution board with IP-42 protection (Metal Door) suitable for 3 phase ELCB / RCCB / FP Isolator as incomer and 10kA SP MCBs as outing going including internal connection and labour charges for surface / flush mounting etc., complete.
| A | 40A FP Isolator - 1 No for incomer, 10kA-6-32A SP MCBs - 12Nos for outgoing.
Taking Output = each
a) Material
|  | 4way TPN, D.B with IP-42 Protection (MD) suitable for 3 phase ELCB / RCCB/ FP Isolator as incommer. | each | 1
|  | 40A, 4 Pole Isolator / ELCB / RCCB | each | 1
|  | 10kA - 6-32A range SP MCBs | each | 12
b) Labour charges :
|  | Skilled Electrician | day | 0.5
|  | Semi Skilled Electrician | day | 1
|  | Helpers | day | 1
|  | Sundries such as TW Plugs, Screws Cement etc, | LS
Rate per each
Note : Labour Charges considered for 2 jobs / day
| B | 63A FP Isolator - 1 No for incomer, 10kA-6-32A SP MCBs - 12Nos for outgoing.
Taking Output = each
a) Material
|  | 4way TPN, D.B with IP-42 Protection (MD) suitable for 3 phase ELCB / RCCB/ FP Isolator as incommer. | each | 1
|  | 63A, 4 Pole Isolator / ELCB / RCCB | each | 1
|  | 10kA - 6-32A range SP MCBs | each | 12
b) Labour charges :
|  | Skilled Electrician | day | 0.5
|  | Semi Skilled Electrician | day | 1
|  | Helpers | day | 1
|  | Sundries such as TW Plugs, Screws Cement etc, | LS
Rate per each
Note : Labour Charges considered for 2 jobs / day
| C | 80A FP Isolator - 1 No for incomer, 6-32A SP MCBs - 18Nos for outgoing.
Taking Output = each
a) Material
|  | 6 way TPN, D.B with IP-42 Protection (MD) suitable for 3 phase ELCB / RCCB/ FP Isolator as incommer. | each | 1
|  | 80A, 4 Pole Isolator / ELCB / RCCB | each | 1
|  | 10kA - 6-32A range SP MCBs | each | 18
b) Labour charges :
|  | Skilled Electrician | day | 0.5
|  | Semi Skilled Electrician | day | 1
|  | Helpers | day | 1
|  | Sundries such as TW Plugs, Screws Cement etc, | LS
Rate per each
Note : Labour Charges considered for 2 jobs / day
| 4.4.5 | Supply and fixing TPN - Vertical type Distribution board with IP - 20 Protection suitable for 3 phase ELCB / RCCB / FP Isolator as incomer and 10 kA TP / SP MCBs as outing going including internal connection and labour charges for surface / flush mounting etc., complete.
| A | Incomer : 63A FP Isolator / ELCB / RCCB
Outgoing : 32A TP MCBs 2 Nos and 6-32A SP MCBs 6 Nos
a) Material
|  | 4way TPN - Vertical type DB with IP-20 protection suitable for 3 Phase ELCB / RCCB / 4 Pole Isolator as in commer and TP / SP MCBs as outgoing with Bus-bar arrangment etc., | Nos | 1
|  | 63Apms, 4 Pole Isolator / ELCB / RCCB | Nos | 1
|  | 32A TP MCBs | Nos | 2
|  | 10kA -6-32A SP MCBs | Nos | 6
b) Labour charges :
|  | Skilled Electrician | day | 0.5
|  | Semi Skilled Electrician | day | 1
|  | Helpers | day | 1
|  | Sundries, suchas T.W plugs, Screws, Cement etc, | LS
Rate per each
Note : Labour Charges considered for 2 jobs / day
| B | Incomer : 80A FP Isolator / ELCB / RCCB
Outgoing : 32A TP MCBs 4 Nos and 6-32A SP MCBs 12Nos
a) Material
|  | 8way TPN - Vertical type DB with IP-20 protection suitable for 3 Phase ELCB / RCCB / 4 Pole Isolator as in commer and TP / SP MCBs as outgoing with Bus-bar arrangment etc., | Nos | 1
|  | 80 Apms, 4 Pole Isolator / ELCB / RCCB | Nos | 1
|  | 32A TP MCBs | Nos | 4
|  | 10kA -6-32A SP MCBs | Nos | 8
b) Labour charges :
|  | Skilled Electrician | day | 0.5
|  | Semi Skilled Electrician | day | 1
|  | Helpers | day | 1
|  | Sundries, suchas T.W plugs, Screws, Cement etc, | LS
Rate per each
Note : Labour Charges considered for 2 jobs / day
| 4.4.6 | Supply and fixing TPN - Vertical type Distribution board with IP - 42 Protection (Metal Door) suitable for 3 phase ELCB / RCCB / FP Isolator as incomer and 10 kA TP / SP MCBs as outing going including internal connection and labour charges for surface / flush mounting etc., complete.
| A | Incomer : 63A FP Isolator/ ELCB / RCCB
Outgoing : 32A TP MCBs 2 Nos and 6-32A SP MCBs 6 Nos
a) Material
|  | 4way TPN - Vertical type DB with IP-42 (Metal Door) protection suitable for 3 Phase ELCB / RCCB / 4 Pole Isolator as in commer and TP / SP MCBs as outgoing with Bus-bar arrangment etc., | Nos | 1
|  | 63Apms, 4 Pole Isolator / ELCB / RCCB | Nos | 1
|  | 32A TP MCBs | Nos | 2
|  | 10kA -6-32A SP MCBs | Nos | 6
b) Labour charges :
|  | Skilled Electrician | day | 0.5
|  | Semi Skilled Electrician | day | 1
|  | Helpers | day | 1
|  | Sundries, suchas T.W plugs, Screws, Cement etc, | LS
Rate per each
Note : Labour Charges considered for 2 jobs / day
| B | Incomer : 80A FP Isolator/ ELCB / RCCB
Outgoing : 32A TP MCBs 4 Nos and 6-32A SP MCBs 12 Nos
a) Material
|  | 8way TPN - Vertical type DB with IP-42 (MD) protection suitable for 3 Phase ELCB / RCCB / 4 Pole Isolator as in commer and TP / SP MCBs as outgoing with Bus-bar arrangment etc., | Nos | 1
|  | 80 Apms, 4 Pole Isolator / ELCB / RCCB | Nos | 1
|  | 32A TP MCBs | Nos | 4
|  | 10kA -6-32A SP MCBs | Nos | 8
b) Labour charges :
|  | Skilled Electrician | day | 0.5
|  | Semi Skilled Electrician | day | 1
|  | Helpers | day | 1
|  | Sundries, suchas T.W plugs, Screws, Cement etc, | LS
Rate per each
Note : Labour Charges considered for 2 jobs / day
| 4.4.7 | Supply and fixing 7 Segment, TPN Distribution board with IP-42 Protection (Metal door) with phase segregation and separation between incoming and outgoing suitable for 3 Phase ELCB / RCCB / FP Isolator as incomer and DP Isolator / RCCB for phase control with 10kA SP MCCB as outgoing including internal connection and labour charges for surface / flush mounting etc., complete.
| A | Incomer : 63A FP Isolator/ ELCB / RCCB
Phase Control : 40A DP Isolator 3 Nos
Outgoing : 10kA 6-32A SP MCBs 12 Nos
a) Material
|  | 7 Segment, TPN Distribution 4Way DB with IP-42 (Metal Door) protection with phase segregation and seperation between incomming an outgoing. | Nos | 1
|  | 63A, 4 Pole Isolator / ELCB / RCCB . | Nos | 1
|  | 40A DP Isolator | Nos | 3
|  | 6-32 Amps range SP MCBs. | Nos | 12
b) Labour charges :
|  | Skilled Electrician | day | 0.5
|  | Semi Skilled Electrician | day | 1
|  | Helpers | day | 1
|  | Sundries such as T.W. Plugs, Screws, Cement etc., | LS
Rate per each
Note : Labour Charges considered for 2 jobs / day
| B | Incomer : 80A FP Isolator/ ELCB / RCCB
Phase Control : 63A DP Isolator 3 Nos
Outgoing : 10kA-6-32A SP MCBs 24 Nos
a) Material
|  | 7 Segment, TPN Distribution 8 Way DB with IP-42 (Metal Door) protection with phase segregation and seperation between incomming an outgoing. | Nos | 1
|  | 80A, 4 Pole Isolator / ELCB / RCCB . | Nos | 1
|  | 63A DP Isolator | Nos | 3
|  | 6-32 Amps range SP MCBs. | Nos | 12
b) Labour charges :
|  | Skilled Electrician | day | 1
|  | Semi Skilled Electrician | day | 1
|  | Helpers | day | 1
|  | Sundries such as T.W. Plugs, Screws, Cement etc., | LS
Rate per each
Note : Labour Charges considered for 2 jobs / day
| 4.4.8 | Supply and fixing TPN - Vertical type Distribution board with IP -42 Protection (Metal Door) with 125A, 4Pole 25 kA MCCB as incomer with 4Nos 32A TP MCBs and 12 Nos. 10 kA SPMCBs as outgoing including internal connection and labour charges for surface / flush mounting etc., complete.
a) Material
|  | 8 Way TPN Vertical DB with IP -42 (Metal door) protection suitable for 125A, 4 Pole, 16kA MCCB as incomer. | Nos | 1
|  | 125 Amps, 4 Pole , 25 kA MCCB | Nos | 1
|  | 10 kA, 32A TP MCBs: | Nos | 4
|  | 10kA, 6 to 32A SP MCBs: Rs.119 / Each | Nos | 12
b) Labour charges :
|  | Skilled Electrician | day | 1
|  | Semi Skilled Electrician | day | 1
|  | Helpers | day | 1
|  | Sundries such as T.W. Plugs, Screws, Cement etc., | LS
Rate per each
Note : 1. Labour Charges considered for 2 jobs / day
2. If the Distribution Boards from Item No. 4.4.1 to 4.4.8 proposed for concealing, add the following:
a 1No. Semi skilled mason
b 1/4 bag cement
| 4.4.9 | Supply and fixing Distribution board with 20A single phase plug and Socket, in sheet steel enclosure with 10/16/20A SP MCB including internal connection and labour charges for surface / flush mounting etc., complete
a) Material
|  | 1 Phase Distribution board with 20A plug and socket. | Nos | 1
|  | 10/16/20A SP MCB | Nos | 1
b) Labour charges :
|  | Skilled Electrician | Nos | 0.25
|  | Semi skilled Electrician | Nos | 0.25
|  | Helpers | Nos | 0.25
|  | Sundries such as Cement, Sand, T.W. Plugs, Screws etc., | LS
Rate per each
Note : 1. Labour Charges considered for 4 jobs / day
2. For concealing, add the following:
a 1No. Semi skilled mason
b 1/4 bag cement
| 4.4.10 | Supply and fixing Distribution board with 20A 3 phase plug and Socket, in sheet steel enclosure with 16/20A TP MCB including internal connection and labour charges for surface / flush mounting etc., complete.
a) Material
|  | Distribution board with 3 Ph. 20A Plug and Socket . | Each | 1
|  | 32A TP MCB, 10 kA | Each | 1
b) Labour charges :
|  | Skilled Electrician | Nos | 0.33
|  | Semi skilled Electrician | Nos | 0.33
|  | Helpers | Nos | 0.33
Sundries such as Cement, T.W. Plugs, Screws etc.,
Rate per each
Note : 1. Labour Charges considered for 3 jobs / day
2. For concealing, add the following:
a 1No. Semi skilled mason
b 1/4 bag cement
BLD-ELEC-5 | 5 | EARTHING
BLD-ELEC-5-1 | 5.1 | EARTHING
| 5.1.1 | Providing independent earthling by excavating a trench to a depth of 2.1 M in all soils, as per size specified in the Data, using 40mm dia 'B' class GI pipe of 2.5 Mtrs length with necessary accessories with hume pipe ring duly providing staggered holes including filling with equal proportion of Salt and Charcoal in layers and all labour charges etc., complete for small quarters.
a) Material
|  | Earth Work Excavation of Hard gravel Soil with small boulder for trench 1st step of size 1.5 x 0.6 x 0.9 m (5'x2'x3') | cum | 0.85
|  | Excavation of Hard disteggrated rocks and boulders for trench 2nd Step of size 1.2 x 0.6 x 1.2 m (Civil SSR) (4'x2'x4') | cum | 0.9
25% extra for narrow trench & pit and back filling with Sand, Coke, Salt etc., and leveling
|  | 40mm dia 'B' Class G.I pipe | Mtr | 2.5
|  | 25 x 6 mm (1"X 1/4") G.I Flat duly drilled 12mm holes (4 Nos) of 200 mm (8") length | Each | 1
|  | Drilling of 16 Nos through holes of 12mm dia to G.I pipe | Each | 16
|  | G.I Nuts, Bolts an Washers | Set | 4
|  | 18" dia hume pipe ring | Each | 1
|  | Hard Coke | Kg | 40
|  | Salt | Kg | 20
|  | b) labour charges for fixing pipe ring and connections | Each
|  | Semi skilled Electrician | Nos | 0.5
|  | Helpers | Nos | 0.5
Sundries
Rate per each
| 5.1.2 | Providing independent earthing for Important equipment with 40mm dia 'B' class 2.5m long G.I pipe and 19mm dia 'B' class G.I pipe of 0.3mtr. long connected with reducer providing G.I funnel with mesh enclosed in C.C.Chamber of 400m x 400m x 400mm with R.C.C. Slab cover duly providing staggered holes filling with salt and charcoal from the bottom of the pipe giving earth connection from electrode through G.I strip of 25 x 6mm x 200mm length with all accessories and labour charges complete, as per IS specifications 732/1982 (Part II)
a) Material
|  | Earth work excavation of hard gravel soil with small boulders for trench 1st step of size 1.5 x 0.9 x 0.9 m (5'x3'x3') | cum | 1.27
|  | Earth work hard disintegrated rock and boulders for trench 2nd Step of size 1.2 x 0.9 x 1.65 m (Civil SSR-16) (4'x3'x5.5') | cum | 1.87
25% extra for trenches and narrow Pit, back filling and blending.
|  | Laying C.C bed in Cement mortar with 1: 2:4 with 20 mm HBG Stone Metal (Civil SSR). | cum | 0.9
|  | Masonary through with brick Masonry with CM 1:3 | cum | 0.23
|  | Cement plastering inside through with 1:3 Cement mortar, 12 mm thick (Civil SSR). | sqm | 2.09
|  | 40mm dia G.I pipe Class 'B' (Civil SSR) | Mtr | 2.5
|  | 19mm dia G.I pipe | Mtr | 0.3
|  | 40mm x 19mm reducer | Each | 1
|  | G.I Funel covered with wire mesh | Each | 1
|  | 25mm x 6mm x 200 mm length G.I Strip (Flat) with 4 Nos. Holes of 12mm dia. | Each | 1
|  | Drilling of staggered holes of 12mm dia to G.I pipe. | Each | 16
|  | G.I Bolts, Nuts and Washers. | Set | 4
|  | Hard Coke. | kg | 4
|  | Salt. | kg | 20
|  | Cost Iron cover 400 mm x 400mm x 50mm. | L.S
b) labour charges for fixing pipe
|  | Skilled Electrician | Nos | 1
Sundries such as Lugs and Saddles
Rate per each
| 5.1.3 | Providing independent earthing for Sophisticated Electronic equipment with 600mm x 600mm x 3.15mm thick copper plate rigidly fixed to 40mm dia G.I Pipe of 0.3mtr. length connected with reducer providing G.I funnel with wiremesh as per National Electric Code including C.C.Chamber of size 400m x 400m x 400mm covered with R.C.C. Slab filling with salt and charcoal giving earth connection from electrode G.I strip of 25mm x 6mm x 200mm length with all accessories and labour charges complete as per IS specification 732/1982 (Part II).
a) Material
|  | Earth work excavation of hard gravel soil with small boulders for trench 1st step of size 1.5 x 0.9 x 0.9 m (5'x3'x3') | cum | 1.27
|  | Earth work hard disintegrated rock and boulders for trench 2nd Step of size 1.2 x 0.9 x 1.65 m (Civil SSR-16) (4'x3'x5.5') | cum | 1.87
25% extra for trenches and narrow Pit, back filling and blending.
|  | Laying C.C bed in Cement mortar with 1: 2:4 with 20 mm HBG Stone Metal (Civil SSR). | cum | 0.9
|  | Masonary through with brick Masonry with CM 1:3 | cum | 0.23
|  | Cement plastering inside through with 1:3 Cement mortar, 12 mm thick (Civil SSR). | sqm | 2.09
|  | 40mm dia G.I pipe Class 'B' (Civil SSR) | Mtr | 2.5
|  | 19mm dia G.I pipe | Mtr | 0.3
|  | 40mm x 19mm reducer | Each | 1
|  | G.I Funel covered with wire mesh | Each | 1
|  | 25mm x 6mm x 200 mm length G.I Strip (Flat) with 4 Nos. Holes of 12mm dia. | Each | 1
|  | 600mm x600mm x 3.15mm thick copper plate | kg | 10
|  | Drilling of staggered holes of 12mm dia to G.I pipe. | Each | 16
|  | G.I Bolts, Nuts and Washers. | Set | 4
|  | Hard Coke. | kg | 4
|  | Salt. | kg | 20
|  | Cost Iron cover 400 mm x 400mm x 50mm. | L.S
b) labour charges for fixing pipe
|  | Skilled Electrician | Nos | 1
Sundries such as Lugs and Saddles
Rate per each
BLD-ELEC-5-2 | 5.2 | G.I Wire and Strip
| 5.2.1 | Supply and Run of No.8 SWG G.I wire including cost of all accessories and labour charges etc., complete.
a) Material
|  | No.8 SWG G.I wire 100 M Length (0.104 Kg / Mtr) | Kg | 10.4
|  | U' Nails | 100Nos | 1.5
b) labour charges
|  | Helpers | day | 2
Sundries.
C) Cost for 100 M
Rate per mtr c/100
| 5.2.2 | Supply and Run of No.10 SWG G.I wire including cost of all accessories and labour charges etc., complete.
a) Material
|  | No.10 SWG G.I wire 100 M Length (0.067 Kg / Mtr) | Kg | 6.7
|  | U' Nails | 100Nos | 1.5
b) labour charges
|  | Helpers | day | 2
Sundries.
C) Cost for 100 M
Rate per mtr c/100
| 5.2.3 | Supply and Run of No.12 SWG G.I wire including cost of all accessories and labour charges etc., complete.
a) Material
|  | No.12 SWG G.I wire 100 M Length (0.044 Kg / Mtr) | Kg | 4.4
|  | U' Nails | 100Nos | 1.5
b) labour charges
|  | Helpers | day | 2
Sundries.
C) Cost for 100 M
Rate per mtr c/100
| 5.2.4 | Supply and Run of No.14 SWG G.I wire including cost of all accessories and labour charges etc., complete.
a) Material
|  | No.14 SWG G.I wire 100 M Length (0.026 Kg / Mtr) | Kg | 2.6
|  | U' Nails | 100Nos | 1.5
b) labour charges
|  | Helpers | day | 2
Sundries.
C) Cost for 100 M
Rate per mtr c/100
| 5.2.5 | Supply and Run of 25mm x 6mm G.I Strip including cost of all accessories and labour charges etc., complete.
a) Material
|  | 25mm x 6mm G.I Strip 100 M Length (1.18 Kg / Mtr) | kg | 118
b) labour charges
|  | Skilled Electrician | Nos | 2
|  | Helper | Nos | 2
Sundries such as T&P.
C) Cost for 100 M
Rate per mtr c/100
| 5.2.6 | Supply and Run of 40mm x 6mm G.I Strip including cost of all accessories and labour charges etc., complete
a) Material
|  | 40mm x 6mm G.I Strip 100 M Length (1.88 Kg / Mtr) | kg | 188
b) labour charges
|  | Skilled Electrician | Nos | 2
|  | Helper | Nos | 2
Sundries such as T&P.
C) Cost for 100 M
Rate per mtr c/100
| 5.2.7 | Supply and Run of 50mm x 6mm G.I Strip including cost of all accessories and labour charges etc., complete.
a) Material
|  | 50mm x 6mm G.I Strip 100 M Length (2.36 Kg / Mtr) | kg | 236
b) labour charges
|  | Skilled Electrician | Nos | 2
|  | Helper | Nos | 2
Sundries such as T&P.
C) Cost for 100 M
Rate per mtr c/100
BLD-ELEC-5-3 | 5.3 | Copper wire and Strip
| 5.3.1 | Supply and Run of Zero gauge copper wire including cost of all accessories and labour charges etc., complete
a) Material
|  | O' SWG Copper wire (0.455 Kg/Mtr.) 100 M Length | Kg | 45.5
b) labour charges
|  | Skilled Electrician | Nos | 1
|  | Semi skilled Electrician | Nos | 1
|  | Helper | Nos | 1
Sundries such as T&P and rounding off
C) Cost for 100 M
Rate per mtr c/100
| 5.3.2 | Supply and Run of No. 8 SWG copper wire including cost of all accessories and labour charges etc., complete.
a) Material
|  | 8 SWG Copper wire (0.1155 Kg/Mtr.) 100 M Length | Kg | 11.55
b) labour charges
|  | Skilled Electrician | Nos | 1
|  | Semi skilled Electrician | Nos | 1
|  | Helper | Nos | 1
Sundries such as T&P and rounding off
C) Cost for 100 M
Rate per mtr c/100
| 5.3.3 | Supply and Run of No. 14 SWG copper wire including cost of all accessories and labour charges etc., complete
a) Material
|  | 14 SWG Copper wire (0.028 Kg/Mtr.) 100 M Length | Kg | 2.8
b) labour charges
|  | Skilled Electrician | Nos | 1
|  | Semi skilled Electrician | Nos | 1
|  | Helper | Nos | 1
Sundries such as T&P and rounding off
C) Cost for 100 M
Rate per mtr c/100
| 5.3.4 | Supply and Run of 25mm x 3mm copper strip including cost of all accessories and labour charges etc., complete.
a) Material
|  | 25mmx 3mm Copper strip (0.663 Kg / Mtr) 100 M Length | Kg | 66.3
b) labour charges
|  | Skilled Electrician | Nos | 2
|  | Helper | Nos | 2
Sundries and rounding off
C) Cost for 100 M
Rate per mtr c/100
| 5.3.5 | Supply and Run of 32mm x 6mm copper strip including cost of all accessories and labour charges etc., complete. | LS
a) Material
|  | 32mmx 6mm Copper strip (1.697 Kg / Mtr) 100 M Length | Kg | 169.7
b) labour charges
|  | Skilled Electrician | Nos | 2
|  | Helper | Nos | 2
Sundries and rounding off
C) Cost for 100 M
Rate per mtr c/100
BLD-ELEC-6 | 6 | SERVICE MAINS & LTOH Lines
BLD-ELEC-6-1 | 6.1 | WPSC (Weather Prrof Single Core) (PVC Cleats)
| 6.1.1 | Supply and Run of 2 of 2.5 Sq.mm WPSC (Whether Proof Single Core) Aluminium cable along with No.10 SWG G.I bearer wire through PVC cleats with all accessories including labour charges etc., complete for service mains.
a) Material
|  | 2.5 Sq.mm WPSC Aluminium cable | 100 M | 2
|  | No.10 SWG G.I wire. (0.026 Kg / Mtr) Length 100 RM | kg | 6.7
|  | PVC Cleats | 100 Nos | 1
b) labour charges
|  | Skilled Electrician | day | 1
|  | Semi skilled | day | 1
|  | Helper | day | 1
Sundries such as insulation tapes and rounding off
C) Cost for 100 M
Rate per mtr c/100
| 6.1.2 | Supply and Run of 2 of 6 Sq.mm WPSC Aluminium cable along with No.10 SWG G.I bearer wire through PVC cleats with all accessories including labour charges etc., complete for service mains.
a) Material
|  | 6 Sq.mm WPSC Aluminium cable | 100 M | 2
|  | No.10 SWG G.I wire. (0.026 Kg / Mtr) Length 100 RM | kg | 6.7
|  | PVC Cleats | 100 Nos | 1
b) labour charges
|  | Skilled Electrician | day | 1
|  | Semi skilled | day | 1
|  | Helper | day | 1
Sundries such as insulation tapes and rounding off
C) Cost for 100 M
Rate per mtr c/100
| 6.1.3 | Supply and Run of 2 of 10 Sq.mm WPSC Aluminium cable along with No.10 SWG G.I bearer wire through PVC cleats with all accessories including labour charges etc., complete for service mains.
a) Material
|  | 10 Sq.mm WPSC Aluminium cable | 100 M | 2
|  | No.10 SWG G.I wire. (0.026 Kg / Mtr )Length 100 RM | kg | 6.7
|  | PVC Cleats | 100 Nos | 1
b) labour charges
|  | Skilled Electrician | day | 1
|  | Semi skilled | day | 1
|  | Helper | day | 1
Sundries such as insulation tapes and rounding off
C) Cost for 100 M
Rate per mtr c/100
| 6.1.4 | Supply and Run of 4 of 6 Sq.mm WPSC Aluminium cable along with No.10 SWG G.I bearer wire on both sides through PVC cleats with all accessories including labour charges etc., complete for service mains.
a) Material
|  | 6 Sq.mm WPSC Aluminium cable | 100 M | 4
|  | No.10 SWG GI Wire (6.7kg x 2) Length 200 RM | kg | 13.4
|  | Binding wire | kg | 0.25
|  | PVC Cleats / Separters 4 W. | 100 Nos | 1
b) labour charges
|  | Skilled Electrician | day | 2
|  | Semi skilled | day | 2
|  | Helper | day | 2
Sundries such as insulation tapes and rounding off
C) Cost for 100 M
Rate per mtr c/100
| 6.1.5 | Supply and Run of 4 of 10 Sq.mm WPSC Aluminium cable along with No.10 SWG G.I bearer wire on both sides through PVC cleats with all accessories including labour charges etc., complete for service mains.
a) Material
|  | 10 Sq.mm WPSC Aluminium cable | 100 M | 4
|  | No.10 SWG GI Wire (6.7kg x 2) Length 200 RM | kg | 13.4
|  | Binding wire | kg | 0.25
|  | PVC Cleats / Separters 4 W. | 100 Nos | 1
b) labour charges
|  | Skilled Electrician | day | 2
|  | Semi skilled | day | 2
|  | Helper | day | 2
Sundries such as insulation tapes and rounding off
C) Cost for 100 M
Rate per mtr c/100
| 6.1.6 | Supply and Run of 4 of 16 Sq.mm WPSC Aluminium cable along with No.10 SWG G.I bearer wire through PVC cleats with all accessories including labour charges etc., complete for service mains.
a) Material
|  | 16 Sq.mm WPSC Aluminium cable | 100 M | 4
|  | No.10 SWG GI Wire (6.7kg x 2) Length 200 RM | kg | 13.4
|  | Binding wire | kg | 0.25
|  | PVC Cleats / Separters 4 W. | 100 Nos | 1
b) labour charges
|  | Skilled Electrician | day | 2
|  | Semi skilled | day | 2
|  | Helper | day | 2
Sundries such as insulation tapes and rounding off
C) Cost for 100 M
Rate per mtr c/100
BLD-ELEC-6-2 | 6.2 | WPTC (Weather Prrof Twin Core) Cable
| 6.2.1 | Supply and Run of 1 of 6 Sq.mm WPTC Aluminium cable along with No.10 SWG G.I bearer wire through PVC cleats with all accessories including labour charges etc., complete.
a) Material
|  | 6 Sq.mm (7/18) wptc Aluminium cable | 100 M | 1
|  | No.10 G.I wire. Length 100 RM | kg | 6.7
|  | Insulation tapes | each | 2
|  | Aluminium link clips | box | 2
b) labour charges
|  | Skilled Electrician | day | 1
|  | Semi skilled | day | 1
|  | Helper | day | 1
Sundries and rounding off
C) Cost for 100 M
Rate per mtr c/100
| 6.2.2 | Supply and Run of 1 of 10 Sq.mm WPTC Aluminium cable along with No.10 SWG G.I bearer wire through PVC cleats with all accessories including labour charges etc., complete.
a) Material
|  | 10 Sq.mm (7/18) wptc Aluminium cable | 100 M | 1
|  | No.10 G.I wire. Length 100 RM | kg | 6.7
|  | Insulation tapes | each | 2
|  | Aluminium link clips | box | 2
b) labour charges
|  | Skilled Electrician | day | 1
|  | Semi skilled | day | 1
|  | Helper | day | 1
Sundries and rounding off
C) Cost for 100 M
Rate per mtr c/100
| 6.2.3 | Supply and Run of 2 of 6 Sq.mm WPTC Aluminium cable along with No.10 SWG G.I bearer wire through PVC cleats with all accessories including labour charges etc., complete.
a) Material
|  | 6 Sq.mm (7/18) wptc Aluminium cable | 100 M | 2
|  | No.10 G.I wire. Length 100 RM | kg | 6.7
|  | PVC insulation tapes | each | 4
|  | Link clips | box | 2
b) labour charges
|  | Skilled Electrician | day | 1
|  | Semi skilled | day | 1
|  | Helper | day | 1
Sundries and rounding off
C) Cost for 100 M
Rate per mtr c/100
| 6.2.4 | Supply and Run of 2 of 10 Sq.mm WPTC Aluminium cable along with No.10 SWG G.I bearer wire through PVC cleats with all accessories including labour charges etc., complete
a) Material
|  | 10 Sq.mm (7/18) wptc Aluminium cable | 100 M | 2
|  | No.10 G.I wire. Length 100 RM | kg | 6.7
|  | PVC insulation tapes | each | 4
|  | Link clips | box | 2
b) labour charges
|  | Skilled Electrician | day | 1
|  | Semi skilled | day | 1
|  | Helper | day | 1
Sundries and rounding off
C) Cost for 100 M
Rate per mtr c/100
| 6.2.5 | Supply and Run of 2 of 16 Sq.mm WPTC Aluminium cable along with No.10 SWG G.I bearer wire through PVC cleats with all accessories including labour charges etc., complete.
a) Material
|  | 16 Sq.mm (7/18) wptc Aluminium cable | 100 M | 2
|  | No.10 G.I wire. Length 100 RM | kg | 6.7
|  | PVC insulation tapes | each | 4
|  | Link clips | box | 2
b) labour charges
|  | Skilled Electrician | day | 1
|  | Semi skilled | day | 1
|  | Helper | day | 1
Sundries and rounding off
C) Cost for 100 M
Rate per mtr c/100
BLD-ELEC-6-3 | 6.3 | L.T.O.H. Lines
| 6.3.1 | Supply and fixing of 3 phase, 4 wire angle iron cross arm with 3 Nos shackle / pin insulators for phases and C.I knob for neutral including cost and conveyance of all materials.
a) Material
|  | Angle Iron 38 x 38 x 6 mm (1.5"x1.5"x1/4") | kg | 4.27
|  | Drilling Holes | each | 6
|  | M.S Clamp 25mm x 6mm with bolts and nuts | each | 1
|  | Pin insulators 100 x 80 mm (4"x3 1/2") | each | 3
|  | C.I Nob | each | 1
|  | Cutting of angle Iron and Welding including cost of flat Iron etc., | LS
b) labour charges
|  | Skilled Electrician | day | 0.125
|  | Semi skilled | day | 0.125
Rate per Each
Note : 1. Labour Charges considered for 8 jobs / day
| 6.3.2 | Supply and fixing of single phase, 2 wire angle iron cross arm with 1 Nos shackle / pin insulators for phases and C.I knob for neutral including cost and conveyance of all materials.
a) Material
|  | Angle Iron 38 x 38 x 6 mm (1.5"x1.5"x1/4" (0.61 mt)) | kg | 2.13
|  | Drilling Holes | each | 4
|  | M.S Clamp 25mm x 6mm with bolts and nuts | each | 1
|  | Pin insulators 100 x 80 mm (4"x3 1/2") | each | 1
|  | C.I Knob | each | 1
|  | Cutting of angle Iron and Welding including cost of flat Iron sundires. | LS
b) labour charges
|  | Skilled Electrician | day | 0.1
|  | Semi skilled | day | 0.1
Rate per Each
Note : 1. Labour Charges considered for 10 jobs / day
| 6.3.3 | Supply and fixing of stayset with 7/8 SWG (10to 15m long) guy insulator with concreting 1:3:6 incluidng excavation of pit and back filling including cost and conveyance of all materials and labolur charges etc., complete.
a) Material
|  | Stay rod of 16mm dia (7/8 SWG) 1560mm length with bolts and nuts with switch plate. | each | 1
|  | Stay tight set (Jum Bracket 300mm) | pair | 1
|  | Stay wire 7/20 weighing 4kgs | each | 1
|  | Cement Concrete 1:3:6 (As per Civil SSR) | cum | 0.142
|  | Excavation of pit and back filling 1.5 x 0.75 x 0.6 m (5'x2.5'x2') | cum | 0.675
|  | Stay clamp with bolts and nuts | set | 1
|  | L.T guy insulator | each | 1
b) labour charges
|  | Skilled Electrician. | day | 0.5
|  | Man Mazdoor | day | 1
Rate per Each
Note : 1. Labour Charges considered for 2 jobs / day
| 6.3.4 | Supply and fixing of over head line horizontal type safety device with angle iron cross arm of size 50 x 50 x 6 mm, 1.52m length projection from pole with 38 x 38 x 6 mm (1 1/2"x1 1/2" x 1/4") angle iron arm including G.I wire for earth continuity and cost of all accessories labour charges etc., complete.
a) Material
|  | 50 x 50 x 6 mm (2"x2"x1/4") Angle Iron of 1.52 Mtr length | kg | 5.32
|  | 38 x 38 x 6 mm (1.5"x1.5"x1/4") Angle Iron of 0.45 Mtr | kg | 1.57
|  | Special Flat Iron Clamp 25x6mm with bolts and nuts | each | 1
|  | No.8 SWG G.I wire 8m Length | kg | 0.8
b) labour charges
|  | Skilled Electrician | day | 0.25
|  | Semi skilled | day | 0.25
|  | Helper | day | 0.5
Sundires such as bolts, nuts including soldering.
Rate per Each
Note : 1. Labour Charges considered for 4 jobs / day
| 6.3.5 | OH Conductors
| 6.3.5 (a) | Supply and erecting 7/2.00 AAAC (All Aluminium Annealed Conductor) / Squirrel (20 Sq.mm) conductor for Overhead line with stringing, binding and suitable size of clamps for Jumpering etc., complete
a) Material
|  | 7/2.0 AAAC (Squirrel) | km | 1
|  | 7/2.0 AAAC for binding and Jumpering. | km | 0.1
|  | Aluminium Clamps | each | 10
b) labour charges
|  | Skilled Electrician | day | 2
|  | Helper | day | 8
|  | For special T&P | LS
Sundires and rounding off
Rate per km
| 6.3.5 (b) | Supply and erecting 7/2.50 AAAC / Weasel (34 Sq.mm) conductor for Overhead line with stringing, binding and suitable size of clamps for Jumpering etc., complete.
a) Material
|  | 7/2.5 AAAC / Weasel (34 Sq.mm) | km | 1
|  | 7/2.5 AAAC for binding and Jumpering. | km | 0.1
|  | Aluminium Clamps | each | 10
b) labour charges
|  | Skilled Electrician | day | 2
|  | Helper | day | 8
|  | For special T&P | LS
Sundires and rounding off
Rate per km
| 6.3.5 (c) | Supply and erecting 7/3.15 AAAC / Rabbit (55 Sq.mm) conductor for Overhead line with stringing, binding and suitable size of clamps for Jumpering etc., complete.
a) Material
|  | 7/3.15 AAAC / Rabbit (55 Sq.mm) | km | 1
|  | 7/3.15 AAAC for binding and Jumpering. | km | 0.1
|  | Aluminium Clamps | each | 10
b) labour charges
|  | Skilled Electrician | day | 2
|  | Helper | day | 8
|  | For special T&P | LS
Sundires and rounding off
Rate per km
| 6.3.6 | Supply and erecting of fibre / PVC spacers for L.T Overhead line of 3 to 5 conductors.
a) Material
|  | PVC spacer suitable for 3 to 5 conductos. | each | 1
b) labour charges
|  | Helper | day | 0.2
|  | Special T&P. | LS
Rate per km
Note : 1. Labour Charges considered for 5 jobs / day
| 6.3.7 | Excavation of hard rock or Bituminous road (BT) by chiselling for preparing pit for poles / stay / earth plates / laying pipes, including clearing the site by removing debris and making the site to original position.
a) Material
|  | Cutting B.T road surface (As per Civil SSR) | cum | 1
|  | Excavation of WBM under B.T | cum | 1
Note : Rate shall be as per Civil SSR
| 6.3.8 (a) | Brick Masonry in CM (1:6) with country Bricks traditional size 23 x 11 x 7 cms
Unit = 1cum
a) Material
|  | Bricks traditional size 23 x 11 x 7 cms 2nd class | Nos | 512
|  | Cement Mortar 1:6 | cum | 0.2
b) labour charges
|  | Mason 1st class | day | 0.24
|  | Mason 2nd class | day | 0.56
|  | Mazdoor (unskilled) | day | 1.88
Scaffolding charges
Add 25% extra on labour for isolated work
Rate per cum
| 6.3.8 (b) | Plastering with CM (1:5), 12 mm thick
Unit = 10 sqm
a) Material
|  | Cement Mortor (1:5) | cum | 0.15
b) labour charges
|  | Mason 1st class | day | 0.6
|  | Mazdoor (unskilled) | day | 0.96
Rate per cum
| 6.3.8 (c) | CRS Masonry in CM (1:6) 2nd Sort
Unit = 1cum
a) Material
|  | Coursed Rubble Stone | cum | 0.94
|  | Bond Stones 7Nos 0.24 x 0.24 x 0.39 = 0.16cum | cum | 0.16
|  | Cement Mortar 1:6 | cum | 0.32
b) labour charges
|  | Mason 1st class | day | 0.45
|  | Mason 2nd class | day | 1.05
|  | Mazdoor (unskilled) | day | 2.32
Add 25% extra on labour for isolated work
Rate per cum
| 6.3.9 (a) | Supply Transportation and unloading the 9.1mtr long PSCC poles with 300kg working load at site in good condition for H.T. / L.T. lines support including cost and conveyance of all materials and labour charges etc., complete.
a) Material
|  | 9.1 Mtr PSCC pole of 300 Kg working load | each | 1
Transportation Charges @ 5% of Cost
|  | Helper for Unloading | day | 0.5
Rate per each
Note : 1. Unloading Charges considered for 12 jobs / 6 Helpers / day
| 6.3.9 (b) | Supply Transportation and unloading the 9.1mtr long PSCC poles with 280kg working load at site in good condition for H.T. / L.T. lines support including cost and conveyance of all materials and labour charges etc., complete.
a) Material
|  | 9.1 Mtr PSCC pole of 280 Kg working load | each | 1
Transportation Charges @ 5% of Cost
|  | Helper for Unloading | day | 0.5
Rate per each
Note : 1. Unloading Charges considered for 12 jobs / 6 Helpers / day
| 6.3.9 (c) | Supply Transportation and unloading the 8.0mtr long PSCC poles with 200kg working load at site in good condition for H.T. / L.T. lines support including cost and conveyance of all materials and labour charges etc., complete.
a) Material
|  | 8 Mtr PSCC pole of 200 Kg working load | each | 1
Transportation Charges @ 5% of Cost
|  | Helper for Unloading | day | 0.5
Rate per each
Note : 1. Unloading Charges considered for 12 jobs / 6 Helpers / day
| 6.3.9 (d) | Supply, Transportation and unloading the 8.0mtr long PSCC poles with 140kg working load at site in good condition for H.T. / L.T. lines support including cost and conveyance of all materials and labour charges etc., complete.
a) Material
|  | 8 Mtr PSCC pole of 140 Kg working load | each | 1
Transportation Charges @ 5% of Cost
|  | Helper for Unloading | day | 0.5
Rate per each
Note : 1. Unloading Charges considered for 12 jobs / 6 Helpers / day
| 6.3.10 (a) | Supply Transportation and unloading the RS Joist of 9.0 mtr long 175mm x 85mm size at site in good condition for H.T. / L.T. lines support including cost and conveyance of all materials and labour charges etc., complete.
a) Material
|  | 175mm x 85mm, 9.0 Mtr long R.S.Joist (1mt = 19.6 Kg) | kg | 176.4
Transportation Charges @ 5% of Cost
|  | Helper for Unloading | day | 0.33
Rate per each
Note : 1. Unloading Charges considered for 20 jobs / 6 Helpers / day
| 6.3.10 (b) | Supply Transportation and unloading the RS Joist of 8.0 mtr long 150mm x 75mm size at site in good condition for H.T. / L.T. lines support including cost and conveyance of all materials and labour charges etc., complete.
a) Material
|  | 150mm x 75mm, 8.0 Mtr long R.S.Joist (1mt = 15.0 Kg) | kg | 120
Transportation Charges @ 5% of Cost
|  | Helper for Unloading | day | 0.33
Rate per each
Note : 1. Unloading Charges considered for 20 jobs / 6 Helpers / day
BLD-ELEC-7 | 7 | STREET LIGHT LUMINARIES
BLD-ELEC-7-1 | 7.1 | FLOURESCENT LUMINAIRE
| 7.1.1 | Supply of 1x40W weatherproof flourescent streetlight fitting comprising canopy of sheet Aluminium in stove enamel finish with copper / VPIT ballast, capacitor, tube and starter etc., complete.
a) Material
|  | 1x40W WP flourscent street light fitting. | each | 1
|  | Lamp cost of 40W | each | 1
Sundries and rounding off
Rate per each
| 7.1.2 | Supply of 2x11W CFL (Compacted Flourescent Lamp), Street light fitting with all standard accessories and 2 Nos 11W CFL, Lamp etc., complete.
a) Material
|  | 2x11W CFL street light fitting. | each | 1
|  | Cost of 11W CFL | each | 1
Sundries and rounding off
Rate per each
| 7.1.3 | Supply of 1x18W CFL, Street light fitting with all standard accessories and 1 No 18W CFL lamp etc., complete.
a) Material
|  | 1x18W CFL street light flourscent fitting. | each | 1
|  | Lamp cost of 1x18W CFL | each | 1
Sundries and rounding off
Rate per each
BLD-ELEC-7-2 | 7.2 | Mercury Vapour (M.V.) LUMINAIRE
| 7.2.1 | Supply of single piece die cast Aluminium body with 80W mercury vapour luminaire with copper wound ballast and capacitor including 80W M.V.Lamp etc., complete.
a) Material
|  | 80W MV Lamp fitting single piece die cast Aluminium body with copper wound ballast and capacitor | each | 1
|  | 80W MV lamp | each | 1
Sundries and rounding off
Rate per each
| 7.2.2 | Supply of single piece die cast Aluminium body with 125W M.V. luminaire with copper wound ballast and capacitor including 125W HPMV lamp etc., complete.
a) Material
|  | 125W MV Lamp fitting single piece die cast Aluminium body with copper wound ballast and capacitor | each | 1
|  | 125W MV lamp | each | 1
Sundries and rounding off
Rate per each
BLD-ELEC-7-3 | 7.3 | High Pressure Sodium Vapour (S.V.) LUMINAIRE
| 7.3.1 | Supply of Integral street light luminaire of 70W HPSV lamp fitting comprises of single piece die cast Aluminium body with copper wound ballast and capacitor, Ignitor, with pot optics including 70W HPSV lamp etc., complete.
a) Material
|  | 70W HPSV Lamp fitting single piece die cast Aluminium body with copper wound ballast and capacitor, Ignitor, with pot optics | each | 1
|  | 70W HPSV lamp | each | 1
Sundries and rounding off
Rate per each
| 7.3.2 | Supply of Integral street light luminaire of 150W HPSV lamp fitting comprises of single piece die cast Aluminium body with copper wound ballast and capacitor, Ignitor, with pot optics including 150W HPSV lamp etc., complete.
a) Material
|  | 150W HPSV Lamp fitting single piece die cast Aluminium body with copper wound ballast and capacitor, Ignitor, with pot optics | each | 1
|  | 156W HPSV lamp | each | 1
Sundries and rounding off
Rate per each
| 7.3.3 | Supply of Integral street light luminaire of 250W HPSV lamp fitting comprises of single piece die cast Aluminium body with copper wound ballast and capacitor, Ignitor, with pot optics including 250W HPSV lamp etc., complete.
a) Material
|  | 250W HPSV Lamp fitting single piece die cast Aluminium body with copper wound ballast and capacitor, Ignitor, with pot optics | each | 1
|  | 250W HPSV lamp | each | 1
Sundries and rounding off
Rate per each
BLD-ELEC-7-4 | 7.4 | METAL HALIDE LUMINAIRE
| 7.4.1 | Supply of Integral street light luminaire of 70W MH lamp fitting comprises of single piece die cast Aluminium body with copper wound ballast and capacitor, Ignitor, with pot optics including 70W MH lamp etc., complete
a) Material
|  | 70W MH Lamp fitting single piece die cast Aluminium body with copper wound ballast and capacitor, Ignitor, with pot optics | each | 1
|  | 70W MH lamp | each | 1
Sundries and rounding off
Rate per each
| 7.4.2 | Supply of Integral street light luminaire of 150W MH lamp fitting comprises of single piece die cast Aluminium body with copper wound ballast and capacitor, Ignitor, with pot optics including 150W MH lamp etc., complete.
a) Material
|  | 150W MH Lamp fitting single piece die cast Aluminium body with copper wound ballast and capacitor, Ignitor, with pot optics | each | 1
|  | 150W MH lamp | each | 1
Sundries and rounding off
Rate per each
| 7.4.3 | Supply of Integral street light luminaire of 250W MH lamp fitting comprises of single piece die cast Aluminium body with copper wound ballast and capacitor, Ignitor, with pot optics including 250W MH lamp etc., complete.
a) Material
|  | 250W MH Lamp fitting single piece die cast Aluminium body with copper wound ballast and capacitor, Ignitor, with pot optics | each | 1
|  | 250W MH lamp | each | 1
Sundries and rounding off
Rate per each
| 7.4.4 | Supply of integral street light luminaire of 250W MH with IP-65 protection, POT optics comprises of single piece die cast Aluminium body with copper wound ballast and capacitor with 250W MH lamp etc., complete.
a) Material
|  | 250W IP-65 MH Lamp fitting single piece die cast Aluminium body with copper wound ballast and capacitor | each | 1
|  | Lamp cost of 250W MH lamp | each | 1
Sundries and rounding off
Rate per each
BLD-ELEC-7-5 | 7.5 | POST TOP LUMINAIRE
| 7.5.1 | Supply of post top luminaire of mushroom type with clear acrylic cover and comprises of control gear capsule die cast Aluminium alloy with VPIT / copper ballast suitable for 9/11/13W CFL with lamp etc., complete.
a) Material
|  | 1X9/11/13W CFL Lamp fitting | each | 1
|  | 1X9/11/13W CFL Lamp | each | 1
Sundries and rounding off
Rate per each
| 7.5.2 | Supply of 125W HPMV integral post top luminaire with Aluminium canopy and acrylic diffuser with all standard accessories and 125W HPMV lamp etc., complete.
a) Material
|  | 125W HPMV post top Lamp fitting | each | 1
|  | Cost of 125W HPMV post top LAMP | each | 1
Sundries and rounding off
Rate per each
| 7.5.3 | Supply of 70W HPSV integral post top luminaire with Aluminium canopy and acrylic diffuser with all standard accessories and 70W HPSV lamp etc., complete.
a) Material
|  | 70W HPSV post top Lamp fitting | each | 1
|  | Cost of 70W HPSV post top lamp | each | 1
Sundries and rounding off
Rate per each
| 7.5.4 | Supply of diamond / sphere type 80W HPMV post top lantern luminaire with all standard accessories including 80W M.V. lamp etc., complete
a) Material
|  | 80W HPMV post top diamond / sphere type Lamp fitting | each | 1
|  | 80W HPMV post top diamond / sphere type Lamp | each | 1
Sundries and rounding off
Rate per each
| 7.5.6 | Supply of diamond / sphere type 125W HPMV post top lantern luminaire with all standard accessories including 125W M.V. lamp etc., complete.
a) Material
|  | 125W HPMV post top Lamp fitting | each | 1
|  | 125W HPMV post top Lamp | each | 1
Sundries and rounding off
Rate per each
| 7.5.7 | Supply of diamond / sphere type 70W HPSV post top lantern luminaire with all standard accessories including 70W S.V. lamp etc., complete.
a) Material
|  | 70W HPSV diamond / sphere post top Lamp fitting | each | 1
|  | 70W HPSV diamond / sphere post top Lamp | each | 1
Sundries and rounding off
Rate per each
BLD-ELEC-7-6 | 7.6 | Well Glass Luminaires
| 7.6.1 | Supply of 80W M.V integral wellglass luminaries with all standard accessories and 80W MV lamp etc., complete.
a) Material
|  | 80W MV wellglass luminaries | each | 1
|  | 80W MV wellglass luminaries lamp | each | 1
Sundries and rounding off
Rate per each
| 7.6.2 | Supply of 70W S.V. integral wellglass luminaries with all standard accessories and 70W S.V. lamp etc., complete.
a) Material
|  | 70W SV wellglass luminaires | each | 1
|  | 70W SV wellglass luminaries. | each | 1
Sundries and rounding off
Rate per each
BLD-ELEC-7-7 | 7.7 | Flood Light Luminaires
| 7.7.1 | Supply of 500W Halogen fitting with all accessories including 500W Halogen lamp etc., complete.
a) Material
|  | 500W halogen lamp fitting. | each | 1
|  | 500W halogen lamp | each | 1
Sundries and rounding off
Rate per each
| 7.7.2 | Supply of 1000W Halogen fitting with all accessories including 1000W Halogen lamp etc., complete.
a) Material
|  | 1000W halogen lamp fitting. | each | 1
|  | 1000W halogen lamp | each | 1
Sundries and rounding off
Rate per each
| 7.7.3 | Supply of integral type flood light metal halide luminaire of 250W comprising of die cast Aluminium housing and a heat resistant toughned glass firmly fixed by means of gasket and toggles with IP-65 protection incluidng control gear housing and all accessories with 250W MH-T lamp etc., complete.
a) Material
|  | 250W MH flood light fitting | each | 1
|  | 250W MH lamp. | each | 1
Sundries and rounding off
Rate per each
| 7.7.4 | Supply of integral type flood light metal halide luminaire of 400W comprising of die cast Aluminium housing and a heat resistant toughned glass firmly fixed by means of gasket and toggles with IP-65 protection incluidng control gear housing and all accessories with 400W MH-T lamp etc., complete.
a) Material
|  | 400W MH flood light fitting | each | 1
|  | 400W MH flood light lamps | each | 1
Sundries and rounding off
Rate per each
BLD-ELEC-7-8 | 7.8 | Labour Charges
| 7.8.1 | Fixing of CFL luminaire (Down lights / Mirror optic / Ornamental type fitting with all necessary accessories in false ceiling / on wall including giving connections and all labour charges etc., complete.
a) Material
|  | 23/0060 twin core flexible copper cable | M | 1
|  | screws with rawal plugs | each | 2
|  | Aluminium flat / cement and sand etc., labour charges. | LS
b) Labour charges.
|  | Skilled Electrician/carpenter | day | 0.066
|  | Semi skilled Electrician / Helper | day | 0.066
Rate per each
Note : Labour Charges considered for15 fixtures / day .
| 7.9.2 | Fixing of 70W MH down light and control gear box with necessary accessories in false ceiling including giving connections and all labour charges etc., complete.
a) Material
|  | 23/0060 twin core flexible copper cable | M | 1
|  | screws with rawal plugs | each | 2
|  | Aluminium flat / cement and sand etc., labour charges. | LS
b) Labour charges
|  | Skilled Electrician/carpenter | day | 0.125
|  | Semi skilled Electrician / Helper | day | 0.125
Rate per each
Note : Labour Charges considered for 8 fixtures / day .
| 7.9.3 | Fixing of 40W tube light luminaire on wall / Ceiling with / TW round blocks with all accessories including giving connections and all labour charges etc., complete.
a) Material
|  | 23/0060 twin core flexible copper cable | M | 1
|  | screws with rawal plugs | each | 2
|  | T.W round blocks | each | 2
|  | Cement and sand etc., | LS
b) Labour charges
|  | Skilled Electrician/carpenter | day | 0.1
|  | Semi skilled Electrician / Helper | day | 0.1
Rate per each
Note : Labour Charges considered for 10 fixtures / day .
| 7.9.4 | Fixing of 40W tube lights with 1/2 Mtr conduit suspension arrangements from ceiling with hooks etc., including giving connections and all labour charges etc., complete.
a) Material
|  | 20mm dia No.16 gauge conduit pipe . | M | 1
|  | 23/0060 twin core flexible copper cable | each | 1
|  | Anchor screws / Hooks / Sockets & Check | each | 2
b) Labour charges
|  | Skilled Electrician/carpenter | day | 0.166
|  | Semi skilled Electrician / Helper | day | 0.166
Rate per each
Note : Labour Charges considered for 6 fixtures / day .
| 7.9.5 | Fixing of 40W street light luminaire to the wall with 1.0 Mtr., 25mm dia GI pipe bracket and anti tilting MS flat etc., including giving connections and labour charges etc., complete.
a) Material
|  | 25mm dia G.I pipe | M | 1
|  | 23/0060 twin core flexible copper cable | M | 2
|  | Pipe bending charges | LS
|  | M.S flat and welding charges | LS
b) Labour charges
|  | Skilled Electrician/carpenter | day | 0.2
|  | Mason | day | 0.2
|  | Semi skilled Electrician / Helper | day | 0.2
Rate per each
Note : Labour Charges considered for 5 fixtures / day .
| 7.9.6 | Fixing of CFL street light luminary with 1.0 Mtr., 25mm dia GI pipe bracket and anti tilting MS flat etc., including giving connections and labour charges etc., complete.
a) Material
|  | 25mm dia G.I pipe | M | 1
|  | 23/0060 twin core flexible copper cable | M | 2
|  | Pipe bending charges | LS
|  | M.S flat and welding charges | LS
b) Labour charges
|  | Skilled Electrician/carpenter | day | 0.125
|  | Mason | day | 0.125
|  | Helper | day | 0.125
Rate per each
Note : Labour Charges considered for 8 fixtures / day .
| 7.9.7 | Fixing of mirror optic tube light luminaire in false ceiling / pop with necessary arrangment including giving connections and all labour charges etc., complete.
a) Material
|  | 28/0060 twin core flexible copper cable | M | 1
|  | Aluminium flat (as per requirment) | LS
b) Labour charges for cutting P.O.P / false ceiling and Fixing MOT
|  | Skilled Electrician | day | 0.125
|  | Carpenter | day | 0.125
|  | Semi skilled Electrician / Helper | day | 0.125
Rate per each
Note : Labour Charges considered for 8 Nos MOT lights in a day
| 7.9.8 | Fixing of MV / SV/MH luminaire on wall with 1.0mt 40mm dia GI pipe bracket and anti-tilting MS flat, 2.5 Sq.mm flexible copper cable etc.,including all labour charges for mason work and giving connections etc., complete.
a) Material
|  | 40mm G.I pipe for Bracket | M | 1
|  | 2.5 Sq.mm flexible copper cable | M | 4
|  | Pipe bending charges | LS
b) Labour charges for Antitiling MS flat / welding charges & fixing
|  | Skilled Electrician | day | 0.25
|  | Carpenter | day | 0.25
|  | Helper | day | 0.25
|  | Welder | day | 0.25
Rate per each
Note : Labour Charges considered for 4Nos MV / SV / MH in a day
Bldngs_Elec-8 | 8 | INTERNAL LUMINAIRE
Bldngs_Elec-8-1 | 8.1.1 | Supply and fixing of single fancy bracket with glass shade and bulb of approved colour and quality etc., by field officers
a) Material
|  | Single Fancy bracket | each | 1
|  | 60W Bulb | each | 1
b) Labour charges
|  | Skilled Electrician | day | 0.04
|  | Helper | day | 0.04
|  | Sundires | LS
Rate per each
Note : Labour Charges considered for 25Jobs per Day
| 8.1.2 | Supply and fixing of double fancy bracket with glass shade and bulb of approved colour and quality etc., by field officers.
a) Material
|  | Double Fancy bracket | each | 1
|  | 60W Bulb | each | 2
b) Labour charges
|  | Skilled Electrician | day | 0.05
|  | Helper | day | 0.05
Sundires
Rate per each
Note : Labour Charges considered for 20Jobs /Day
| 8.1.3 | Supply and fixing 10" ceiling fittings with glass doom and bulb apporved by dept., officers including giving connection etc., complete.
a) Material
|  | 10" Ceiling fitting with glass doom | each | 1
|  | 60W Bulb | each | 1
b) Labour charges
|  | Skilled Electrician | day | 0.05
|  | Helper | day | 0.05
Sundires
Rate per each
Note : Labour Charges considered for 20 Jobs / Day
| 8.1.4 | Supply and fixing of Bulk head fitting with cast Aluminium enamel painted body with water tight, clear glass with wire guard hinged with lock and key arrangements etc., complete with lamp.
a) Material
|  | Bulkhead fitting | each | 1
|  | 60W Bulb | each | 1
b) Labour charges
|  | Skilled Electrician | day | 0.083
|  | Helper | day | 0.083
Sundires such as TW block / screws, cement etc.,
Rate per each
Note : Labour Charges considered for 12 Jobs / Day
Bldngs_Elec-8-2 | 8.2 | Flourescent Luminaire
| 8.2.1 | Supply and transportation of 1x11 W mirror light with all standard accessories diffuser and 1No 11W CFL lamp etc., complete
a) Material
|  | 1x11W M.O. fitting | each | 1
|  | Cost of C.F.L. | each | 1
Sundries and rounding off
Rate per each
| 8.2.2 | Supply and Transportation of 1x36/40W box type tube light luminaire with copper / VPIT Choke, condensor, starters etc., and 1No 36/40W tube etc., complete.
a) Material
|  | 1x40/36 box type T.L fitting | each | 1
|  | 36/40 Tube | each | 1
Sundries and rounding off
Rate per each
| 8.2.3 | Supply and transportation of 2x36/40W box type tube light luminaire with 2Nos copper / VPIT chokes, starters, with condensor and 2Nos 36/40W tube etc., complete.
a) Material
|  | 2x40/36 box type T.L fitting | each | 1
|  | 36/40 FTL | each | 2
Sundries and rounding off
Rate per each
| 8.2.4 | Supply and Transportation of 1x40W patty type tube light luminaire with copper choke, starter etc., including 1No 40W tube etc., complete.
a) Material
|  | 1x40 patty type T.L. fitting | each | 1
|  | 40W FTL | each | 1
Sundires and rounding off
Rate per each
Bldngs_Elec-8-3 | 8.3 | INDUSTRIAL luminaire
| 8.3.1 | Supply and Transportation of white vitreous 1x36 / 40W industrial box type luminaire with Copper / VPIT Choke, Condensor, Starters etc., with reflector including 1No 40W tube etc., complete.
a) Material
|  | 1x36/40W Industrial box type T.L. fitting | each | 1
|  | 36/40W FTL | each | 1
Sundries and rounding off
Rate per each
| 8.3.2 | Supply and Transportation of white vitreous 2x36 / 40W industrial box type luminaire with 2Nos Copper / VPIT Choke, Condensor, Starters etc.,complete with reflector including 2Nos 40W tube etc., complete.
a) Material
|  | 2x36/40W Industrial box type T.L. fitting | each | 1
|  | 36/40W FTL | each | 2
Sundries and rounding off
Rate per each
Bldngs_Elec-8-4 | 8.4 | MIRROR OPTIC luminaire
| 8.4.1 | Supply and Transportation of 2x36 / 40W surface mounting mirror optic luminaire with powder coated CRCA sheet steel housing with Aluminium mirror reflectors with VPIT chokes, Starters, Condensor etc., complete with 2Nos 36/40W tubes etc.,complete.
a) Material
|  | 2x36/40 Surface M.O.L fitting | each | 1
|  | 40/36 FTL | each | 2
Sundries and rounding off
Rate per each
| 8.4.2 | Supply and transportation of 2x36/40W recessed mounting mirror optic (darklite) luminaire with powder coated CRCA sheet steel housing with Aluminium mirror reflector with VPIT Chokes, Starter, Condensor etc., complete with 2Nos 36/40W tubes etc., complete.
a) Material
|  | 2x36/40 Recessed M.O. L fitting | each | 1
|  | 36/40 FTL | each | 2
Sundries and rounding off
Rate per each
| 8.4.3 | Supply and transportation of 2x11W surface mounting mirror optic luminaire with powder coated CRCA sheet steel housing with Aluminium mirror refector with VPIT Chokes and 2Nos 11W CFL lamps etc., complete.
a) Material
|  | 2x11W CFL surface M.O.L fitting | each | 1
|  | 11W CFL | each | 2
Sundries and rounding off
Rate per each
| 8.4.4 | Supply and transportation of 2x11W Recessed type luminaire with powder coated CRCA sheet steel housing with Aluminium mirror refector with VPIT Chokes and 2Nos 11W CFL lamps etc., complete.
a) Material
|  | 2x11W CFL recessed M.O.L fitting | each | 1
|  | 11W cfl | each | 2
Sundries and rounding off
Rate per each
| 8.4.5 | Supply and transportation of 2x36w CFL paralite louvre (P5) recessed low glare mirror optic luminaire comprising bright anodised Aluminium reflector with VPIT Chokes and 36w CFL lamps.
a) Material
|  | 2x36 CFL PS paralite Louvars fitting | each | 1
|  | 36w CFL | each | 2
Sundries and rounding off
Rate per each
| 8.4.6 | Supply and transportation of 3x36w CFL paralite louvre (P5) recessed low glare mirror optic luminaire comprising bright anodised Aluminium reflector with VPIT Chokes and 3x36w CFL lamps.
a) Material
|  | 3x36 CFL PS paralite Louvars fitting | each | 1
|  | 36w CFL | each | 3
Sundries and rounding off
Rate per each
Bldngs_Elec-8-5 | 8.5 | T- 5 Luminaires.
| 8.5.1 | Supply and transportation of 1X28W surface pendant mounting T- 5 extruded Aluminium with Aluminium reflector luminaire with all standard accessories and connections etc., complete with 1 No. 28 W tube
a) Material
|  | 1x28w pendant T5 lugs fitting | each | 1
|  | 28w T5 FTL | each | 1
Sundries and rounding off
Rate per each
| 8.5.2 | Supply and transportation of 2X28W recessed With 2 Nos. pendant mounting low glare T- 5 mirror optic luminaire with electronic Ballasts etc., complete 28w tubes.
a) Material
|  | 2x28w T5 M.O. fitting | each | 1
|  | 28w T5 FTL | each | 2
Sundries and rounding off
Rate per each
Bldngs_Elec-8-6 | 8.6 | C.F.L. Down Lights
| 8.6.1 | Supply and transportation of recessed mounting 1x13W CFL down light with all standard accessories with 1No. 13W CFL lamp (D type) etc., complete.
a) Material
|  | 1x13W CFL Down light fitting | each | 1
|  | 13W CFL | each | 1
Sundries and rounding off
Rate per each
| 8.6.2 | Supply and transportation of recessed mounting 2x13W CFL down light with all standard accessories with 2No. 13W CFL lamp etc., complete.
a) Material
|  | 2x13W CFL Down light fitting | each | 1
|  | 13W CFL | each | 2
Sundries and rounding off
Rate per each
| 8.6.3 | Supply and transportation of recessed mounting 1x18W CFL down light with all standard accessories with 1No. 18W CFL lamp etc., complete.
a) Material
|  | 1x18W CFL Down light fitting | each | 1
|  | 18W CFL | each | 1
Sundries and rounding off
Rate per each
| 8.6.4 | Supply and transportation of recessed mounting 2x18W CFL down light with all standard accessories with 2No. 18W CFL lamp etc., complete.
a) Material
|  | 2x18W CFL Down light fitting | each | 1
|  | 18W CFL | each | 2
Sundries and rounding off
Rate per each
| 8.6.5 | Supply and Transportation recess mounting 70W metal hallide down lighter with control gear and 1No 70W M.H lamp etc., complete.
a) Material
|  | 70W M.H down light fitting | each | 1
|  | 70W M.H lamp | each | 1
Sundries and rounding off
Rate per each
| 8.6.6 | Supply and Transportation of Ceiling / Wall mounted Circular 1x13W luminaire with decorative acrylic diffuser and 1 No. 13W CFL lamp (circular type) etc., complete.
a) Material
|  | 1x13W Circular CFL fitting | each | 1
|  | 13W CFL | each | 1
Sundries and rounding off
Rate per each
| 8.6.7 | Supply and Transportation of Ceiling / Wall mounted Circular 2x13W luminaire with decorative acrylic diffuser and 2 No. 13W CFL lamp (circular type) etc., complete.
a) Material
|  | 2x13W Circular CFL fitting | each | 1
|  | 13W CFL | each | 2
Sundries and rounding off
Rate per each
Bldngs_Elec-8-7 | 8.7 | HALOGEN DOWN LIGHTERS
| 8.7.1 | Supply and Transportation of recess mounting 12v, 50w adjustable halogen down light with white / colour Shade including transformer and 1No 50w halogen lamp etc., complete.
a) Material
|  | 50w Halogen recessed mounting | each | 1
|  | 50w Halogen bulb | each | 1
Sundries and rounding off
Rate per each
| 8.7.2 | Supply and Transportation of recess mounting 12v, 50w Zoom type halogen down light with white / colour Shade including transformer and 1No 50w halogen lamp etc., complete.
a) Material
|  | 50w Halogen zoom type down light. | each | 1
|  | 50w Halogen bulb | each | 1
Sundries and rounding off
Rate per each
Bldngs_Elec-9 | 9 | AIR CONDITIONING & REFRIGERATION
Bldngs_Elec-9-1 | 9.1 | Air-Conditioners
| 9.1.1(a) | Supply and Transportation of Window mounted type, Room Air-Conditioner 1.5 Ton confirming to IS : 1391, Suitable for operation on 230V + 10% 50 Hz.., Single phase, A.C. Supply capable for performing Cooling, Dehumidifying, Air Circulating, Filtering and Ventilation etc., complete.
a) Material
1.5 Ton A.C Unit
ADD : Duties & Taxes as applicable
|  | Transportation on Material |  | 2%
Rate per each
| 9.1.1(b) | Supply and Transportation of Window mounted type, Room Air-Conditioner 2.0 Ton confirming to IS : 1391, Suitable for operation on 230V + 10% 50 Hz.., Single phase, A.C. Supply capable for performing Cooling, Dehumidifying, Air Circulating, Filtering and Ventilation etc., complete.
a) Material
2.0 Ton A.C Unit
ADD : Duties & Taxes as applicable
|  | Transportation on Material |  | 2%
Rate per each
| 9.1.2 (a) | Supply and Transportation of 1.5 Ton Split type Air-Conditiner, fitted with Hermetically sealed compressor, Operating on refrigerant R-22 / Non - CFC High wall mounting confirming to IS : 1391, suitable for operation on 230V, 50 Hz.., Single phase, A.C Supply capable of performing Cooling, Dehumidifying, Air Circulating, Filtering with cooling and condensing units, with 5 Mtr of required size of copper piping duly insulated and 3 core copper flexible chord of required length etc., complete.
a) Material
1.5 Ton Split A.C Unit ABS (Plastic Cabin)
ADD : Duties & Taxes as applicable
|  | Transportation on Material |  | 2%
Rate per Each
| 9.1.2 (b) | Supply and Transportation of 2.0 Ton Split type Air-Conditiner, fitted with Hermetically sealed compressor, Operating on refrigerant R-22 / Non - CFC High wall mounting confirming to IS : 1391, suitable for operation on 230V, 50 Hz.., Single phase, A.C Supply capable of performing Cooling, Dehumidifying, Air Circulating, Filtering with cooling and condensing units, with 5 Mtr of required size of copper piping duly insulated and 3 core copper flexible chord of required length etc., complete.
a) Material
2.0 Ton Split ABS Plastic Cabin A.C Unit
ADD : Duties & Taxes as applicable
|  | Transportation on Material |  | 2%
Rate per Each
| 9.1.3 | Installation Charges for 1/0 / 1.5 / 2.0 Ton Window type room Air-Conditioner with insulating foam, testing and commissioning etc., complete.
a) Material
Installation Charges of Window type A.C.Unit. (as per observed Data)
Rate per Each
| 9.1.4 | Installation Charges for 1.5 / 2.0 Ton Split Air-Conditioner with foam, insulation for copper pipings connected for the Indoor and outdoor unit including testing and commissioning etc., complete.
a) Material
Installation Charges of 1/5 / 2.0 Ton Split A.C.Unit. (As per observed Data )
Rate per Each
| 9.1.5 | Supply, Fabrication and installation of well seasoned T.W. frame of size 685 x 483 mm (27" x 19") ( with section size of 75 x 100 mm (3" x 4" T.W.)) for 1.0 / 1.5 / 2.0 Ton Window A.C.Unit duly making necessary provision in the wall / Window with cost and conveyance of all materials etc., complete
a) Material
|  | Well seasoned wooden frame for Window A.C Units | cum | 0.018
b) Labour charges for fabrication & Fixing
|  | Carpenter | day | 0.5
|  | Mason | day | 0.5
|  | Helper | day | 0.5
|  | Making necessary provision in wall / window with Hardware | LS
Rate per Each
Note : Labour is Considered for 2 jobs / day
| 9.1.6 | Supply, Fabrication and installation of 38 x 38 x 6 mm (1.5" x 1 1/2" x 1/4") M.S. angle Iron frame suitable for condensing Unit for Split A.C including 2 Coats of Red oxide the followed by 2 coats enamel paint etc., complete.
a) Material
|  | 38 x 38 x 6 mm (1.5" x 1 /12" x 1/4") angle iron frame, 13 M length (1 Mtr = 3.5 Kgs) | kg | 10.5
|  | Fabrication charges including Painting | kg | 10.5
b) Labour charges for Fixing
|  | Carpenter | day | 0.25
|  | Mason | day | 0.25
|  | Helper | day | 0.25
|  | Sundires such as cement etc. | LS
Rate per Each
Note : Labour is Considered for 4 jobs / day
| 9.1.7 | Supply and Installation of copper tubing between indoor and outdoor unit for split Air-Conditioner including foaming etc., complete.
a) Material
Copper tubing between indoor and outdoor units inlcuding foaming
b) Labour charges for cutting, bending, welding etc.,
|  | Welder | day | 0.04
|  | Helper | day | 0.04
Rate per Metre
Note : Labour is Considered for 25 M / day
Bldngs_Elec-9-2 | 9.2 | REPAIRS TO AIR - CONDITIONERS
| 9.2.1 | Replacement of defective compressor by supply of 1.0 / 1.5 Ton brand new sealed compressor ISI Mark
a) Material
|  | Supply of brand new.1/ 1.5 Ton compressor ISI Mark | each | 1
b) Labour charges
|  | Skilled Electrician | day | 0.5
|  | Helper | day | 0.5
|  | Transportation on Material |  | 2%
Rate per Each
Note : Labour is Considered for 2 jobs / day
| 9.2.2 | Replacement of defective compressor by supply of 2.0 Ton brand new sealed compressor ISI Mark
a) Material
|  | Supply of brand new 2.0 Ton compressor by brand new ISI Mark | each | 1
b) Labour charges
|  | Skilled Electrician | day | 0.5
|  | Helper | day | 0.5
|  | Transportation on Material |  | 2%
Rate per Each
Note : Labour is Considered for 2 jobs / day
| 9.2.3 | Replacement of old and Unserviceable Fan Motor by supply and Installation of new 1/6th H.P multi speed Fan Motor suitable for 1.0 / 1.5 / 2.0 Ton Window A.C.Unit.
a) Material
|  | Supply of 1/6th H.P multispeed Fan Motor for 1.0 / 1.5 / 2.0 T A.C.Unit. | each | 1
b) Labour charges
|  | Skilled Electrician | day | 0.5
|  | Helper | day | 0.5
Rate per Each
Note : Labour is Considered for 2 jobs / day
| 9.2.5 | Replacement of Unserviceable fan motor capacitor 6 mfd by new capacitor for A.C machine of 1.0 1.5 / Ton Capacity.
a) Material
|  | 6 MFD motor capacitor | each | 1
b) Labour charges for removing old one & fixing
|  | Semi skilled Electrician | day | 0.2
Rate per Each
Note : Labour is Considered for 5 jobs / day
| 9.2.6 | Replacement of Unserviceable Thermostat switch by supply and installation of new thermostat switch suitable for 1.0 / 1.5 / 2.0 Ton A.C.Unit.
a) Material
|  | Thermostat switch for 1.0 / 1.5 / 2.0 Ton A.C.Unit. | each | 1
b) Labour charges for removing old one & fixing
|  | Semi skilled Electrician | day | 0.2
Rate per Each
Note : Labour is Considered for 5 jobs / day
| 9.2.7 | Replacement of Unserviceable starting capacitor of 80 to 120 mfd. By new approved make capacitor suitable for compressor motor of 1.0 / 1.5 Ton A.C. Unit.
a) Material
|  | Starting capacitor of 80 to 120 mfd. | each | 1
b) Labour charges for removing old one & fixing
|  | Semi skilled Electrician | day | 0.2
Rate per Each
Note : Labour is Considered for 5 jobs / day
| 9.2.8 | Replacement of unserviceable running capacitor of 36 mfd by new approved make capacitor suitable for compressor motor of 1.0 / 1.5 Ton A.C.Unit.
a) Material
|  | Running capacitor 36 mfd | each | 1
b) Labour charges for removing old one & fixing
|  | Semi skilled Electrician | day | 0.2
Rate per Each
Note : Labour is Considered for 5 jobs / day
| 9.2.9 | Replacement of Unserviceable relay by new approved make having pickup voltage 220 Volts and dropout voltage 120 Volts suitable for 1.0 / 1.50 Ton A.C. Unit.
a) Material
|  | Relay having pickup 220V and dropout voltage 120V | each | 1
b) Labour charges for removing old one & fixing
|  | Semi skilled Electrician | day | 0.2
Rate per Each
Note : Labour is Considered for 5 jobs / day
| 9.2.10 | Replacement of Unserviceable filter and capillary tube by supply and installation of new filter and capillary tube including welding et., complete for 1.0 / 1.5 / 2.0 Ton A.C.Unit.
a) Material
|  | Filter and capillary tube for 1.0 / 1.5/2.0 Ton A.C.Unit | each | 1
b) Labour charges for removing old one & fixing
|  | Semi skilled Electrician | day | 0.2
Rate per Each
Note : Labour is Considered for 5 jobs / day
| 9.2.11 | Replacement of Unserviceable air filter by new air filter suitable for 1.50 Ton A.C.Unit P.V.C. / NYLON for Window A.C.
a) Material
|  | PVC / Nylon Air Filter for Window type A.C.Unit. | each | 1
b) Labour charges for removing old one & fixing
|  | Semi skilled Electrician | day | 0.2
Rate per Each
Note : Labour is Considered for 5 jobs / day
| 9.2.11(a) | Replacement of Unserviceable air filter by new air filter suitable for 1.50 Ton A.C.Unit P.V.C. / NYLON for Split A.C.
a) Material
|  | PVC / Nylon Air Filter for Split type A.C.Unit. | each | 1
b) Labour charges for removing old one & fixing
|  | Semi skilled Electrician | day | 0.2
Rate per Each
Note : Labour is Considered for 5 jobs / day
Bldngs_Elec-9-3 | 9.3 | Refrigerators
| 9.3.1 | Supply Refrigerator domestic type approved make 165 to 310 Ltrs. Storage capacity, suitable for operation on 230 /250 Volts 50 Hz.. complete with automatic temparture control confirming to IS specifications No. 1476 / 79 with one year guarantee for seale unit in refrigeration system including cost and conveyance of all materials and labour charges etc., complete.
a) Material
|  | ----- capacity refrigerator cost | each | 1
|  | Transportation @ 2% of Unit Cost |  | 2%
|  | Loading, Unloading & Instalation @ 2% of Unit Cost |  | 2%
Rate per Each
Bldngs_Elec-9-4 | 9.6 | Stabilizers
| 9.6.1 | Supply and erecting fully automatic line voltage stabilizer for operation on input voltage 200 to 250V. rated for 0.5 KVA maximum load and time delay model with Volt meter, selector switch, 6A / 16A flush type, 5 pin socket for out put and with 3 core flexible chord and 3 pin 6/16A plug top suitable for refrigerator for continuous operation including cost and conveyance of all mateials and all labour charges etc., complete.
a) Material
|  | 0.5 KVA Stabilizer | each | 1
b) Labour Charges
|  | Semi skilled Electrician | day | 0.044
|  | Helper | day | 0.044
|  | Transportation Charges on Unit Cost |  | 2%
Rate per Each
Note : Labour is Considered for 23 jobs / day
| 9.6.2 | Supply and erecting fully automatic line voltage stabilizer for operation on input voltage 200 to 250V. rated for 1 KVA maximum load and time delay model with Volt meter, selector switch, 6A / 16A flush type, 5 pin socket for out put and with 3 core flexible chord and 3 pin 6/16A plug top suitable for refrigerator for continuous operation including cost and conveyance of all mateials and all labour charges etc., complete.
a) Material
|  | 1 KVA Stabilizer | each | 1
b) Labour Charges
|  | Semi skilled Electrician | day | 0.044
|  | Helper | day | 0.044
|  | Transportation Charges on Unit Cost |  | 2%
Rate per Each
Note : Labour is Considered for 23 jobs / day
| 9.6.3 | Supply and erecting fully automatic line voltage stabilizer for operation on input voltage 200 to 250V. rated for 3 KVA / 4 KVA / 5 KVA maximum load and time delay model with Volt meter, selector switch, 6A / 16A flush type, 5 pin socket for out put and with 3 core flexible chord and 3 pin 6/16A plug top suitable for refrigerator for continuous operation including cost and conveyance of all mateials and all labour charges etc., complete.
a) Material
|  | 3 KVA / 4 KVA / 5 KVA Stabilizer | each | 1
b) Labour Charges
|  | Skilled Electrician | day | 0.1
|  | Helper | day | 0.1
|  | Transportation Charges on Unit Cost |  | 2%
Rate per Each
Note : Labour is Considered for 10 jobs / day
Bldngs_Elec-9-5 | 9.7 | Fans
| 9.7.2 | Supply of 900 mm (36") / 1200 mm (48") / 1400 mm (56") sweep 230V, A.C 50 Hz.Ceiling fan with 3 Blades and double ball bearings with all standard accessories.
a) Material
|  | 900 mm (36") / 1200 mm (48") / 1400 mm (56") Ceiling Fan | each | 1
|  | Transportation Charges on Unit Cost |  | 1%
Rate per Each
| 9.7.7 | Supply and erecting wall mounting fan 400mm (16") / 450 mm (18") sweep A.C. 50Hz.. 1350 r.p.m oscillating type with regulator.
a) Material
|  | 400mm (16") / 450 mm (18") wall mounting Fan | each | 1
b) Labour Charges
|  | Semi Skilled Electrician | day | 0.1
|  | Helper | day | 0.1
Rate per Each
Note : Labour is Considered for 10 jobs / day
| 9.7.10 | Supply of pedastal fan (16") 400mm, 250 Volts, 50Hz. oscillating type complete with all standard accessories.
a) Material
|  | 400mm (16") Pedastal Fan | each | 1
|  | Transportation Charges on Unit Cost |  | 2%
Rate per Each
| 9.7.16 | EXHAUST FANS
Supply of fresh air exhaust fan of light duty 250V A.C.50Hz.. 225 mm (9") / 300mm size (12") 1350 R.P.M Metallic body plastic blades, wire mesh, etc., complete.
a) Material
|  | 225 mm (9") / 300mm (12") L.D. Exhaust Fan | each | 1
|  | Transportation Charges on Unit Cost |  | 1%
Rate per Each
| 9.7.18 | Supply of fresh air exhaust fan of Heavy duty 250V A.C.50Hz.. 300mm size (12") / 375 mm (15") 900 R.P.M etc., complete.
a) Material
|  | 300mm (12") / 375 mm (15") H.D. Exhaust Fan | each | 1
|  | Transportation Charges on Unit Cost |  | 1%
Rate per Each
| 9.7.24 | Supply and erecting fan hook of 12/15mm dia M.S. rod / bar grouted in RCC slab with making the slab as original.
a) Material
|  | 12/15mm plain M.S rod for Fan hook | each | 1
|  | Cement, Sand and Rounding off | LS
b) Labour charges for grouting in RCC slab, Fixing of Fan hook with masonary work.
|  | Mason | day | 0.166
|  | Helper | day | 0.166
Rate per Each
Note : Labour is Considered for 6 jobs / day
| 9.7.25 | Supply and erecting 19/20mm steel tube down rod of one meter length with bolts & nuts duly painted with matching colour of fan complete
a) Material
|  | 19/20mm steel tube down rod with bolts & nuts for fan with maching colour. | M | 1
b) Labour charges for Fixing
|  | Helper | day | 0.1
Rate per Each
Note : Labour is Considered for 10 jobs / day
| 9.7.26 | Supply and erecting resistance type regulator for ceiling fans 900/1200/1400mm sweep complete erected on existing board.
a) Material
|  | Resistance type Regulator | M | 1
b) Labour charges.
|  | Semi skilled Electrician | day | 0.1
Rate per Each
Note : Labour is Considered for 10 jobs / day
| 9.7.33 | Cleaning of Ceiling fan in existing position .
Labour charges for cleaning greasing / oilingoverhauling
|  | Helper | day | 0.2
Rate per Each
Note : Labour is Considered for 10 jobs / day by 2 helpers
| 9.7.34 | Removing the ceiling fan and refixing after overhauling and greasing the bearings and replacement of wire leads etc complete
a) Material
|  | 23/0060 twin core wire | M | 1
b) Labour charges.
Removing and refixing of ceiling fan after overhauling
|  | Semi skilled Electrician | day | 0.166
|  | Helper | day | 0.166
|  | sundries | LS
Rate per Each
Note : Labour is Considered for 6 jobs / day
| 9.7.35 | Labour Charges
Labour charges for Fixing of Ceiling fan and regulator including transportation and giving connections with twin core wire etc., complete.
a) Material
|  | 23/0060 Twin Core wire | M | 1
|  | Unforseen item works, such as painting to down rod, screws etc., | LS
b) Labour charges.
|  | Skilled Electrician | day | 0.125
|  | Helper | day | 0.125
Rate per Each
Note : Labour is Considered for 8 fans / day
| 9.7.36 | Labour charges for fixing of Exhaust fan in wall with necessary connections and masonary work of making hole, finishing etc., complete
a) Material
|  | 23/0060 Twin flat wire | M | 1
|  | Cement | kg | 25
b) Labour charges.
|  | Skilled Electrician | day | 0.25
|  | Helper | day | 0.25
|  | Mason | day | 0.25
|  | Sundries such as Sand, Bolt, Nuts etc., | LS
Rate per Each
Note :1. Labour is Considered for 6 jobs / day
2. Cost of louver shutter may be added if required.
3. If hole is already made available, labour charges of Mason shall be deleted.
Bldngs_Elec-10 | 10 | WATER HEATERS
Bldngs_Elec-10-1 | 10.1.2 | Supply and Transportation of stove enamelled storage / pressure type vertical / Horizontal water heater with copper tank 25 / 35 / 50 Ltrs. Capacity with non return valve on inlet side and dead weight pressure reducing valve on outlet side 230/ 250V, single phase 2000 watts heating element, thermostat control, fusible plug, pilot lamp etc., erected and tested complete with ISI specifications etc., including all materials, transportation, and labour charges complete.
a) Material
|  | 25 / 35 / 50 Ltrs. Water Heater | each | 1
|  | Transportation Charges on Unit Cost |  | 2%
Rate per Each
| 10.1.5 | Labour charges for erection of storage water heater with 2Nos Nylon / PVC / Metalic hose pipe etc., on wall duly making necessary fixing arrangments including connections etc., complete.
a) Material
|  | Flexible Nylon / PVC / Metallic hose pipe | each | 2
|  | 50 / 100 mm (2" / 4") long bolt and nut with washers | each | 4
|  | Towards wooden plugs, cement etc., | LS
b) Labour charges.
|  | Skilled Electrician | day | 0.25
|  | Helper | day | 0.5
|  | Semi skilled Mason | day | 0.25
Rate per Each
Note : Labour is Considered for 4 jobs / day
Bldngs_Elec-10-2 | 10.2 | INSTANT WATER HEATERS
| 10.2.1 | Supply and erecting ISI Mark 3KW Instant Water heater with multiple safety system, rust free ABS plastic body, 230V, 50Hz.., A.C. supply with inlet and outlet connections with pvc/ nylon / metallic hose pipe, thermostat control and thermal cutoff with 3 core P.V.C. flexible wire leads duly tested including cost of all materials and all labour charges etc., complete.
a) Material
|  | 3KW Instant Water Heater | each | 1
|  | Transportation Charges on Unit Cost |  | 2%
|  | Hose pipe PVC/ Nylon | each | 2
|  | T.W getting Bolt / Nuts, Cement, Sand etc. | LS
b) Labour charges.
|  | Skilled Electrician | day | 0.25
|  | Helper | day | 0.25
Rate per Each
Note : Labour is Considered for 4 jobs / day
Bldngs_Elec-10-3 | 10.4 | REPAIRS TO WATER HEATERS.
| 10.4.1 | Replacement of unserviceable heating element by new one for 1.5 / 2.0 / 3.0 Kw water heater
a) Material
|  | 2/3 KW heating Element | each | 1
b) Labour charges.
|  | Skilled Electrician | day | 0.2
|  | Sundries and rounding off | LS
Rate per Each
Note : Labour is Considered for 5 jobs / day
| 10.4.2 | Replacement of Unserviceable thermostat by new thermostat with range 30 to 90 C. adjustable and suitable for 25 to 50 Ltrs. Capacity.
a) Material
|  | Thermostat range 30-90 Degree suitable for 25 to 50 Ltrs. | each | 1
b) Labour charges.
|  | Skilled Electrician | day | 0.2
|  | Sundries and rounding off | LS
Rate per Each
| 10.4.5 | Replacing unserviceable pressure release valve by new water heater of 15 to 50 Ltrs.capacity.
a) Material
|  | Pressure release valve for 25 to 50 Ltrs water heater | each | 1
b) Labour charges.
|  | Skilled Electrician | day | 0.2
|  | Sundries and rounding off | LS
Rate per Each
Bldngs_Elec-11 | 11 | WATER PUMPS
Bldngs_Elec-11-1 | 11.1 | Mono-Block Pumps
| 11.1.1 | Supply and erecting approved make centrifugal water pump with impeller, priming funnel cork, companion metallic flanges, with bolts and nuts and mounted on a common shaft of high efficient squirrel cage Induction motor totally enclosed and fan cooled type suitable to operate on 230V, Single phase, 50Hz.. 1440 RPM A.C.Supply of 0.5HP exculding suction / delivery pipe with nuts duly grouted on existing C.C foundation and bolts, spring washers of requisite size for monoblock motor and pump (IS : 9079).
a) Material
|  | 0.5HP, 230V, single phase A.C 50Hz. 1440 RPM with all accessories. Including all taxes | each | 1
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Fitter | day | 0.5
|  | Helper | day | 1
|  | Plumber | day | 0.5
|  | Sundries and rounding off | LS
Rate per Each
Note : Labour is Considered for 2 jobs / day
| 11.1.2 | Supply and erecting approved make centrifugal water pump with impeller, priming funnel cork, companion metallic flanges, with bolts and nuts and mounted on a common shaft of high efficient squirrel cage Induction motor totally enclosed and fan cooled type suitable to operate on 230V, Single phase, 50Hz.. 1440 RPM A.C.Supply of 1HP exculding suction / delivery pipe with nuts duly grouted on existing C.C foundation and bolts, spring washers of requisite size for monoblock motor and pump (IS : 9079).
a) Material
|  | 1 HP, 230V, single phase A.C 50Hz. 1440 RPM with all accessories. Including all taxes | each | 1
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Fitter | day | 0.5
|  | Helper | day | 1
|  | Plumber | day | 0.5
|  | Sundries and rounding off | LS
Rate per Each
| 11.1.3 | Supply and erecting approved make centrifugal water pump with impeller, priming funnel cork, companion metallic flanges, with bolts and nuts and mounted on a common shaft of high efficient squirrel cage Induction motor totally enclosed and fan cooled type suitable to operate on 230V, Single phase, 50Hz.. 1440 RPM A.C.Supply of 1.5 HP exculding suction / delivery pipe with nuts duly grouted on existing C.C foundation and bolts, spring washers of requisite size for monoblock motor and pump (IS : 9079).
a) Material
|  | 1.5 HP, 230V, single phase A.C 50Hz. 1440 RPM with all accessories. Including all taxes | each | 1
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges.
|  | Skilled Fitter | day | 0.5
|  | Helper | day | 1
|  | Plumber | day | 0.5
|  | Sundries and rounding off | LS
Rate per Each
| 11.1.4 | Supply and erecting approved make centrifugal water pump with impeller, priming funnel cork, companion metallic flanges, with bolts and nuts and mounted on a common shaft of high efficient squirrel cage Induction motor totally enclosed and fan cooled type suitable to operate on 230V, Single phase, 50Hz.. 1440 RPM A.C.Supply of 2.0 HP exculding suction / delivery pipe with nuts duly grouted on existing C.C foundation and bolts, spring washers of requisite size for monoblock motor and pump (IS : 9079).
a) Material
|  | 2 HP, 230V, single phase A.C 50Hz. 1440 RPM with all accessories. Including all taxes | each | 1
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Fitter | day | 0.5
|  | Helper | day | 1
|  | Plumber | day | 0.5
|  | Sundries and rounding off | LS
Rate per Each
| 11.1.5 | Supply and erecting approved make centrifugal water pump with impeller, priming funnel cork, companion metallic flanges, with bolts and nuts and mounted on a common shaft of high efficient squirrel cage Induction motor totally enclosed and fan cooled type suitable to operate on 415V, 3 phase, 50Hz.. 2880 RPM A.C.Supply of 3.0HP exculding suction / delivery pipe with nuts duly grouted on existing C.C foundation and bolts, spring washers of requisite size for monoblock motor and pump (IS : 9079).
a) Material
|  | 3 phase, 3 HP, 415V, 50Hz., 2880 RPM centrifugal Water pump with all taxes | each | 1
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Fitter | day | 1
|  | Helper | day | 1
|  | Plumber | day | 1
|  | Sundries and rounding off | LS
Rate per Each
| 11.1.6 | Supply and erecting approved make centrifugal water pump with impeller, priming funnel cork, companion metallic flanges, with bolts and nuts and mounted on a common shaft of high efficient squirrel cage Induction motor totally enclosed and fan cooled type suitable to operate on 415V, 3 phase, 50Hz.. 2880 RPM A.C.Supply of 5HP exculding suction / delivery pipe with nuts duly grouted on existing C.C foundation and bolts, spring washers of requisite size for monoblock motor and pump (IS : 9079).
a) Material
|  | 3 phase, 5 HP, 415V, 50Hz., 2880 RPM centrifugal Water pump with all taxes | each | 1
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Fitter | day | 1
|  | Helper | day | 1
|  | Plumber | day | 1
|  | Sundries and rounding off | LS
Rate per Each
| 11.1.7 | Supply and erecting approved make centrifugal water pump with impeller, priming funnel cork, companion metallic flanges, with bolts and nuts and mounted on a common shaft of high efficient squirrel cage Induction motor totally enclosed and fan cooled type suitable to operate on 415V, 3 phase, 50Hz.. 2880 RPM A.C.Supply of 7.5HP exculding suction / delivery pipe with nuts duly grouted on existing C.C foundation and bolts, spring washers of requisite size for monoblock motor and pump (IS : 9079).
a) Material
|  | 3 phase, 7.5 HP, 415V, 50Hz., 2880 RPM centrifugal mono block pump with all taxes | each | 1
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Fitter | day | 1
|  | Helper | day | 1
|  | Plumber | day | 1
|  | Sundries and rounding off | LS
Rate per Each
| 11.1.8 | Supply and erecting approved make centrifugal water pump with impeller, priming funnel cork, companion metallic flanges, with bolts and nuts and mounted on a common shaft of high efficient squirrel cage Induction motor totally enclosed and fan cooled type suitable to operate on 415V, 3 phase, 50Hz.. 2880 RPM A.C.Supply of 10HP exculding suction / delivery pipe with nuts duly grouted on existing C.C foundation and bolts, spring washers of requisite size for monoblock motor and pump (IS : 9079).
a) Material
|  | 3 phase, 10 HP, 415V, 50Hz., 2880 RPM centrifugal mono block pump with all taxes | each | 1
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Fitter | day | 1
|  | Helper | day | 1
|  | Plumber | day | 1
|  | Sundries and rounding off | LS
Rate per Each
| 11.1.9 | Supply and erecting approved make centrifugal water pump with impeller, priming funnel cork, companion metallic flanges, with bolts and nuts and mounted on a common shaft of high efficient squirrel cage Induction motor totally enclosed and fan cooled type suitable to operate on 415V, 3 phase, 50Hz.. 2880 RPM A.C.Supply of 15HP exculding suction / delivery pipe with nuts duly grouted on existing C.C foundation and bolts, spring washers of requisite size for monoblock motor and pump (IS : 9079).
a) Material
|  | 3 phase, 15 HP, 415V, 50Hz., 2880 RPM centrifugal Water pump with all taxes | each | 1
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Fitter | day | 1
|  | Helper | day | 3
|  | Plumber | day | 1
|  | Sundries and rounding off | LS
Rate per Each
Bldngs_Elec-11-2 | 11.2 | EJECTO PUMPS
| 11.2.1 | Supply and erecting Ejecto type water pump single phase, 0.5HP single stage with brass venturi and having suction pipe 40mm dia, pressure pipe 32mm dia and delivery pipe 32mm dia, with maximum discharge head of 80 feet including transportation of all materials and labour charges etc., complete.
a) Material
|  | 0.5 HP, single phase, 230V, 50Hz. Ejecto type pump set. Including all taxes | each | 1
|  | M.S clamps suitable for 40mmx32mm pipes with nuts and bolts. | each | 2
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Electrician | day | 0.5
|  | Helper | day | 1
|  | Fitter | day | 0.5
|  | Sundries and rouding off | LS
Rate per Each
Note : Labour is Considered for 2 jobs / day
| 11.2.2 | Supply and erecting Ejecto type water pump single phase, 1.0HP single stage with brass venturi and having suction pipe 40mm dia, pressure pipe 32mm dia and delivery pipe 32mm dia, with maximum discharge head of 80feet including transportation of all materials and labour charges etc., complete.
a) Material
|  | 1.0 HP, single phase, 230V, 50Hz. Ejecto type pump set. Including all taxes | each | 1
|  | M.S clamps suitable for 40mmx32mm pipes with nuts and bolts. | each | 2
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Electrician | day | 0.5
|  | Helper | day | 1
|  | Fitter | day | 0.5
|  | Sundries and rouding off | LS
Rate per Each
Note : Labour is Considered for 2 jobs / day
| 11.2.3 | Supply and erecting Ejecto type water pump single phase, 1.5HP single stage with brass venturi and having suction pipe 40mm dia, pressure pipe 32mm dia and delivery pipe 32mm dia, with maximum discharge head of 80 feet including transportation of all materials and labour charges etc., complete.
a) Material
|  | 1.5 HP, single phase, 230V, 50Hz. Ejecto type pump set. Including all taxes | each | 1
|  | M.S clamps suitable for 40mmx32mm pipes with nuts and bolts. | each | 2
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Electrician | day | 0.5
|  | Helper | day | 1
|  | Fitter | day | 0.5
|  | Sundries and rouding off | LS
Rate per Each
Note : Labour is Considered for 2 jobs / day
| 11.2.4 | Supply and erecting Ejecto type water pump single phase, 2.0HP single stage with brass venturi and having suction pipe 40mm dia, pressure pipe 32mm dia and delivery pipe 32mm dia, with maximum discharge head of 80 feet including transportation of all materials and labour charges etc., complete.
a) Material
|  | 2.0 HP, single phase, 230V, 50Hz. Ejecto type pump set. Including all taxes | each | 1
|  | M.S clamps suitable for 40mmx32mm pipes with nuts and bolts. | each | 2
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Electrician | day | 0.5
|  | Helper | day | 1
|  | Fitter | day | 0.5
|  | Sundries and rouding off | LS
Rate per Each
Note : Labour is Considered for 2 jobs / day
| 11.2.6 | Supply and erecting Ejecto type water pump 3 phase, 3 HP single stage with brass venturi and having suction pipe, pressure pipe and delivery pipe, with maximum discharge head of 80 feet , including transportation, and all materials all labour charges etc., complete.
a) Material
|  | 3.0 HP, single phase, 230V, 50Hz. Ejecto type pump set. Including all taxes | each | 1
|  | M.S clamps suitable for 40mmx32mm pipes with nuts and bolts. | each | 2
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Electrician | day | 0.5
|  | Helper | day | 1
|  | Fitter | day | 0.5
|  | Sundries and rouding off | LS
Rate per Each
Note : Labour is Considered for 2 jobs / day
| 11.2.7 | Supply and erecting Ejecto type water pump 3 phase, 5 HP single stage with brass venturi and having suction pipe, pressure pipe and delivery pipe, with maximum discharge head of 80', including transportation, and all materials all labour charges etc., complete.
a) Material
|  | 3Ph, 5 HP 415V, 50Hz. Ejecto pump set with all taxes | each | 1
|  | M.S clamps suitable for Air and delivery pipes with nuts and bolts. | each | 2
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Fitter | day | 0.5
|  | Helper | day | 1.5
|  | Plumber | day | 0.5
|  | Sundries and rouding off | LS
Rate per Each
Note : Labour is Considered for 2 jobs / day
Bldngs_Elec-11-3 | 11.3 | SUBMERSIBLE PUMPS (Bore well type)
| 11.3.1 (a) | Supply and erecting, ISI mark submersible 1.0 HP,Single Phase 18stages pumpset suitable for 106 / 156mm dia borewell with high quality water resistant and dynamically balanced bronze impeller with stainless steel shaft sleeves, pump coupling and pivot of Single phase 250V, 50Hz.. A.C. power supply copper winding with water proof insulation and high precision strength not to be effected by chemical in water and suitable bronze bearings with nut and bolts etc., with necessary H-type clamp of suitable size and strength.
a) Material
|  | 1HP, Single Phase 18 stage submerisible pump set including all taxes | each | 1
|  | Special M.S. clamps with bolts and nuts | each | 2
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Fitter | day | 0.5
|  | Helper | day | 1
|  | Plumber | day | 0.5
|  | Sundries and rouding off | LS
Rate per Each
Note : Labour is Considered for 2 jobs / day
| 11.3.1 (b) | Supply and erecting, ISI mark submersible 1.5 HP, Single Phase 20 stages pumpset suitable for 106 / 156mm dia borewell with high quality water resistant and dynamically balanced bronze impeller with stainless steel shaft sleeves, pump coupling and pivot of Single phase 250V , 50Hz.. A.C. power supply copper winding with water proof insulation and high precision strength not to be effected by chemical in water and suitable bronze bearings with nut and bolts etc., with necessary H-type clamp of suitable size and strength.
a) Material
|  | 1.5HP, Single Phase 20 stage submerisible pump set including all taxes | each | 1
|  | Special M.S. clamps with bolts and nuts | each | 2
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Fitter | day | 0.5
|  | Helper | day | 1
|  | Plumber | day | 0.5
|  | Sundries and rouding off | LS
Rate per Each
Note : Labour is Considered for 2 jobs / day
| 11.3.1 (c) | Supply and erecting, ISI mark submersible 2.0 HP, Single Phase 30 stages pumpset suitable for 106 / 156mm dia borewell with high quality water resistant and dynamically balanced bronze impeller with stainless steel shaft sleeves, pump coupling and pivot of Single phase 250V , 50Hz.. A.C. power supply copper winding with water proof insulation and high precision strength not to be effected by chemical in water and suitable bronze bearings with nut and bolts etc., with necessary H-type clamp of suitable size and strength.
a) Material
|  | 2HP, Single Phase 30 stage submerisible pump set including all taxes | each | 1
|  | Special M.S. clamps with bolts and nuts | each | 2
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Fitter | day | 0.5
|  | Helper | day | 1
|  | Plumber | day | 0.5
|  | Sundries and rouding off | LS
Rate per Each
Note : Labour is Considered for 2 jobs / day
| 11.3.2 | Supply and erecting, ISI mark submersible 2.0 HP, 3 Phase, 3 stages pumpset suitable for 156mm dia borewell with high quality water resistant and dynamically balanced bronze impeller with stainless steel shaft sleeves, pump coupling and pivot of 3 phase 415V , 50Hz.. A.C. power supply copper winding with water proof insulation and high precision strength not to be effected by chemical in water and suitable bronze bearings with nut and bolts etc., with necessary H-type clamp of suitable size and strength.
a) Material
|  | 2HP, 3 Ph 3 stage submerisible pump set including all taxes | each | 1
|  | Special M.S. clamps with bolts and nuts | each | 2
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Fitter | day | 1
|  | Helper | day | 2
|  | Plumber | day | 1
Hire charges of tripod with winch 50% of Labour charges
|  | Sundries and rouding off | LS
Rate per Each
| 11.3.3 | Supply and erecting, ISI mark submersible 3.0 HP,3 Phase, 4 stages pumpset suitable for 156mm dia borewell with high quality wear resistance and dynamically balanced bronze impeller with stainless steel shaft sleeves, pump coupling and pivot of 3 phase 415V , 50Hz.. A.C. power supply copper winding with water proof insulation and high precision strength not to be effected by chemical in water and suitable bronze bearings with nut and bolts etc., with necessary H-type clamp of suitable size and strength.
a) Material
|  | 3HP, 3 Ph 4 stage submerisible pump set. Including all taxes | each | 1
|  | Special M.S. clamps with bolts and nuts | each | 2
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Fitter | day | 1
|  | Helper | day | 2
|  | Plumber | day | 1
Hire charges of tripod with winch 50% of Labour charges
|  | Sundries and rouding off | LS
Rate per Each
| 11.3.4 | Supply and erecting, ISI mark submersible 3 HP, 3 Phase, 6 stages pumpset suitable for 156mm dia borewell with high quality wear resistance and dynamically balanced bronze impeller with stainless steel shaft sleeves, pump coupling and pivot of 3 phase 415V , 50Hz.. A.C. power supply copper winding with water proof insulation and high precision strength not to be effected by chemical in water and suitable bronze bearings with nut and bolts etc., with necessary H-type clamp of suitable size and strength.
a) Material
|  | 3HP, 3 Ph 6 stage submerisible pump set. Including all taxes | each | 1
|  | Special M.S. clamps with bolts and nuts | each | 2
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Fitter | day | 1
|  | Helper | day | 2
|  | Plumber | day | 1
Hire charges of tripod with winch 50% of Labour charges
|  | Sundries and rouding off | LS
Rate per Each
| 11.3.5 | Supply and erecting, ISI mark submersible 3 HP, 3 Phase, 8 stages pumpset suitable for 156mm dia borewell with high quality wear resistance and dynamically balanced bronze impeller with stainless steel shaft sleeves, pump coupling and pivot of 3 phase 415V , 50Hz.. A.C. power supply copper winding with water proof insulation and high precision strength not to be effected by chemical in water and suitable bronze bearings with nut and bolts etc., with necessary H-type clamp of suitable size and strength.
a) Material
|  | 3HP, 3 Ph 6 stage submerisible pump set. Including all taxes | each | 1
|  | Special M.S. clamps with bolts and nuts | each | 2
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Fitter | day | 1
|  | Helper | day | 2
|  | Plumber | day | 1
Hire charges of tripod with winch 50% of Labour charges
|  | Sundries and rouding off | LS
Rate per Each
| 11.3.6 | Supply and erecting, ISI mark submersible 3 HP, 3 Phase, 9 stages pumpset suitable for 156mm dia borewell with high quality wear resistance and dynamically balanced bronze impeller with stainless steel shaft sleeves, pump coupling and pivot of 3 phase 415V , 50Hz.. A.C. power supply copper winding with water proof insulation and high precision strength not to be effected by chemical in water and suitable bronze bearings with nut and bolts etc., with necessary H-type clamp of suitable size and strength.
a) Material
|  | 3HP, 3 Ph 6 stage submerisible pump set Including all taxes | each | 1
|  | Special M.S. clamps with bolts and nuts | each | 2
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Fitter | day | 1
|  | Helper | day | 2
|  | Plumber | day | 1
Hire charges of tripod with winch 50% of Labour charges
|  | Sundries and rouding off | LS
Rate per Each
| 11.3.7 | Supply and erecting, ISI mark submersible 4 HP, 3 Phase, 6 stages pumpset suitable for 156mm dia borewell with high quality wear resistance and dynamically balanced bronze impeller with stainless steel shaft sleeves, pump coupling and pivot of 3 phase 415V, 50Hz.. A.C. power supply copper winding with water proof insulation and high precision strength not to be effected by chemical in water and suitable bronze bearings with nut and bolts etc., with necessary H-type clamp of suitable size and strength.
a) Material
|  | 4HP, 3 Ph 6 stage submerisible pump set including all taxes | each | 1
|  | Special M.S. clamps with bolts and nuts | each | 2
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Fitter | day | 1
|  | Helper | day | 2
|  | Plumber | day | 1
Hire charges of tripod with winch 50% of Labour charges
|  | Sundries and rouding off | LS
Rate per Each
| 11.3.8 | Supply and erecting, ISI mark submersible 4 HP, 3 Phase, 12 stages pumpset suitable for 156mm dia borewell with high quality wear resistance and dynamically balanced bronze impeller with stainless steel shaft sleeves, pump coupling and pivot of 3 phase 415V, 50Hz.. A.C. power supply copper winding with water proof insulation and high precision strength not to be effected by chemical in water and suitable bronze bearings with nut and bolts etc., with necessary H-type clamp of suitable size and strength.
a) Material
|  | 4HP, 3 Ph 12 stages submerisible pump set Including all taxes | each | 1
|  | Special M.S. clamps with bolts and nuts | each | 2
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Fitter | day | 1
|  | Helper | day | 2
|  | Plumber | day | 1
Hire charges of tripod with winch 50% of Labour charges
|  | Sundries and rouding off | LS
Rate per Each
| 11.3.10 | Supply and erecting, ISI mark submersible 5 HP, 3 Phase, 8 stages pumpset suitable for 156mm dia borewell with high quality wear resistance and dynamically balanced bronze impeller with stainless steel shaft sleeves, pump coupling and pivot of 3 phase 415V, 50Hz.. A.C. power supply copper winding with water proof insulation and high precision strength not to be effected by chemical in water and suitable bronze bearings with nut and bolts etc., with necessary H-type clamp of suitable size and strength.
a) Material
|  | Cost of 3 Ph, 5 HP, 8 St. S.M pumpset | each | 1
|  | Special Clamps with Bolts & Nuts | each | 2
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Fitter | day | 2
|  | Helper | day | 3
|  | Plumber | day | 1
Hire charges of tripod with winch 50% of Labour charges
|  | Sundries and rouding off | LS
Rate per Each
| 11.3.11 | Supply and erecting, ISI mark submersible 5 HP, 3 Phase, 13 stages pumpset suitable for 156mm dia borewell with high quality wear resistance and dynamically balanced bronze impeller with stainless steel shaft sleeves, pump coupling and pivot of 3 phase 415V , 50Hz.. A.C. power supply copper winding with water proof insulation and high precision strength not to be effected by chemical in water and suitable bronze bearings with nut and bolts etc., with necessary H-type clamp of suitable size and strength.
a) Material
|  | Cost of 3 Ph, 5 HP, 8 St. S.M pumpset | each | 1
|  | Special Clamps with Bolts & Nuts | each | 2
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Fitter | day | 2
|  | Helper | day | 3
|  | Plumber | day | 1
Hire charges of tripod with winch 50% of Labour charges
|  | Sundries and rouding off | LS
Rate per Each
| 11.3.12 | Supply and erecting, ISI mark submersible 7.5 HP,3 Phase, 6 stages pumpset suitable for 156mm dia borewell with high quality wear resistance and dynamically balanced bronze impeller with stainless steel shaft sleeves, pump coupling and pivot of 3 phase 415V, 50Hz.. A.C. power supply copper winding with water proof insulation and high precision strength not to be effected by chemical in water and suitable bronze bearings with nut and bolts etc., with necessary H-type clamp of suitable size and strength.
a) Material
|  | 3 Ph, 7.5 HP, 6 St. S.M pumpset | each | 1
|  | Special Clamps with Bolts & Nuts | each | 2
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Fitter | day | 2
|  | Helper | day | 3
|  | Plumber | day | 1
Hire charges of tripod with winch 50% of Labour charges
|  | Sundries and rouding off | LS
Rate per Each
| 11.3.13 | Supply and erecting, ISI mark submersible 7.5 HP, 3 Phase, 12 stages pumpset suitable for 156mm dia borewell with high quality wear resistance and dynamically balanced bronze impeller with stainless steel shaft sleeves, pump coupling and pivot of 3 phase 415V , 50Hz.. A.C. power supply copper winding with water proof insulation and high precision strength not to be effected by chemical in water and suitable bronze bearings with nut and bolts etc., with necessary H-type clamp of suitable size and strength.
a) Material
|  | 3 Ph, 7.5 HP, 12 St. S.M pumpset | each | 1
|  | Special Clamps with Bolts & Nuts | each | 2
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Fitter | day | 2
|  | Helper | day | 3
|  | Plumber | day | 1
Hire charges of tripod with winch 50% of Labour charges
|  | Sundries and rouding off | LS
Rate per Each
| 11.3.15 | Supply and erecting, ISI mark submersible 10 HP,3 Phase, 12 stages pumpset suitable for 156mm dia borewell with high quality wear resistance and dynamically balanced bronze impeller with stainless steel shaft sleeves, pump coupling and pivot of 3 phase 415V, 50Hz.. A.C. power supply copper winding with water proof insulation and high precision strength not to be effected by chemical in water and suitable bronze bearings with nut and bolts etc., with necessary H-type clamp of suitable size and strength.
a) Material
|  | Cost of 3 Ph,10 H.P 12St. S.M pumpset | each | 1
|  | Special Clamps with Bolts & Nuts | each | 2
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Fitter | day | 2
|  | Helper | day | 3
|  | Plumber | day | 1
Hire charges of tripod with winch 50% of Labour charges
|  | Sundries and rouding off | LS
Rate per Each
| 11.3.16 | Supply and erecting, ISI mark submersible 10 HP,3 Phase,16 stages pumpset suitable for 156mm dia borewell with high quality wear resistance and dynamically balanced bronze impeller with stainless steel shaft sleeves, pump coupling and pivot of 3 phase 415V, 50Hz.. A.C. power supply copper winding with water proof insulation and high precision strength not to be effected by chemical in water and suitable bronze bearings with nut and bolts etc., with necessary H-type clamp of suitable size and strength.
a) Material
|  | Cost of 3 Ph,10 H.P 16 St. S.M pumpset | each | 1
|  | Special Clamps with Bolts & Nuts | each | 2
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Fitter | day | 2
|  | Helper | day | 3
|  | Plumber | day | 1
Hire charges of tripod with winch 50% of Labour charges
|  | Sundries and rouding off | LS
Rate per Each
| 11.3.17 | Supply and erecting, ISI mark submersible 15 HP, 3 Phase, 15 stages pumpset suitable for 156mm dia borewell with high quality wear resistance and dynamically balanced bronze impeller with stainless steel shaft sleeves, pump coupling and pivot of 3 phase 415V, 50Hz.. A.C. power supply copper winding with water proof insulation and high precision strength not to be effected by chemical in water and suitable bronze bearings with nut and bolts etc., with necessary H-type clamp of suitable size and strength.
a) Material
|  | Cost of 3 Ph,15 H.P 15 St. S.M pumpset | each | 1
|  | Special Clamps with Bolts & Nuts | each | 2
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Fitter | day | 2
|  | Helper | day | 4
|  | Plumber | day | 1
Hire charges of tripod with winch 50% of Labour charges
|  | Sundries and rouding off | LS
Rate per Each
Bldngs_Elec-11-4 | 11.4 | SUB MERSIBLE PUMPS (OPEN WELL)
| 11.4.1 | Supply and erecting ISI make submersible pumpset suitable for erection in open well with water resistant dynamically balanced impeller with stainless steel shaft sleeves, pump coupling and pivot with squirrel cage Induction Motor of 3 phase, 415V, 50Hz.., A.C.Supply, heavy copper windings with water proof insulation and high precision strength not to be effected by chemicals in water with suitable bronze bearings, 3 HP pump erected with necessary H-type clamps of suitable size and strength including cost of all materials, Transportation and labour charges etc., complete.
a) Material
|  | 3 Ph, 3HP Submersible motor | each | 1
|  | Special clamps with nut and bolis | each | 2
MS Girders across the open well to support delivery pipe clamps (as per requirement)
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Fitter | day | 1
|  | Helper | day | 2
|  | Plumber | day | 1
Hire charges of tripod with winch 50% of Labour charges
|  | Sundries and rouding off | LS
Rate per Each
| 11.4.2 | Supply and erecting ISI make submersible pumpset suitable for erection in open well with water resistant dynamically balanced impeller with stainless steel shaft sleeves, pump coupling and pivot with squirrel cage Induction Motor of 3 phase, 415V, 50Hz.., A.C.Supply, heavy copper windings with water proof insulation and high precision strength not to be effected by chemicals in water with suitable bronze bearings, 5 HP pump erected with necessary H-type clamps of suitable size and strength including cost of all materials, Transportation and labour charges etc., complete.
a) Material
|  | 3 Ph, 5HP Submersible motor | each | 1
|  | Special clamps with nut and bolis | each | 2
MS Girders across the open well to support delivery pipe clamps (as per requirement)
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Fitter | day | 1
|  | Helper | day | 2
|  | Plumber | day | 1
Hire charges of tripod with winch 50% of Labour charges
|  | Sundries and rouding off | LS
Rate per Each
| 11.4.3 | Supply and erecting ISI make submersible pumpset suitable for erection in open well with water resistant dynamically balanced impeller with stainless steel shaft sleeves, pump coupling and pivot with squirrel cage Induction Motor of 3 phase, 415V, 50Hz.., A.C.Supply, heavy copper windings with water proof insulation and high precision strength not to be effected by chemicals in water with suitable bronze bearings, 7.5 HP pump erected with necessary H-type clamps of suitable size and strength including cost of all materials, Transportation and labour charges etc., complete.
a) Material
|  | 3 Ph, 7.5HP Submersible motor | each | 1
|  | Special clamps with nut and bolis | each | 2
MS Girders across the open well to support delivery pipe clamps (as per requirement)
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Fitter | day | 1
|  | Helper | day | 2
|  | Plumber | day | 1
Hire charges of tripod with winch 50% of Labour charges
|  | Sundries and rouding off | LS
Rate per Each
| 11.4.4 | Supply and erecting ISI make submersible pumpset suitable for erection in open well with water resistant dynamically balanced impeller with stainless steel shaft sleeves, pump coupling and pivot with squirrel cage Induction Motor of 3 phase, 415V, 50Hz.., A.C.Supply, heavy copper windings with water proof insulation and high precision strength not to be effected by chemicals in water with suitable bronze bearings, 10 HP pump erected with necessary H-type clamps of suitable size and strength including cost of all materials, Transportation and labour charges etc., complete.
a) Material
|  | 3 Ph, 10 HP Submersible motor | each | 1
|  | Special clamps with nut and bolis | each | 2
MS Girders across the open well to support delivery pipe clamps (as per requirement)
|  | Transportation Charges on Unit Cost |  | 2%
b) Labour charges for erection of pump set including pipe connection for suction & delivery
|  | Skilled Fitter | day | 1
|  | Helper | day | 3
|  | Plumber | day | 1
Hire charges of tripod with winch 50% of Labour charges
|  | Sundries and rouding off | LS
Rate per Each
Note:- Above rates of pumpsets are exculding suction & delivery pipes
Bldngs_Elec-11-5 | 11.5 | ACCESSORIES
| 11.5.1 | Providing cement concrete with 1:2:4 foundation for pump and motor with required size and length of foundation bolts and nuts including cost and conveyance of all materials and labour charges etc., complete.
a) Material
Rate as per Civil SSR, since it is a Civil item.
| 11.5.2 | Supplying and erecting D.O.L Starter 250V, Single phase, 50Hz. With SS enclouser comprising of contactor with bi-metalic relay with necessary push buttons, transportation and all labour charges etc., complete .
a) Material
|  | D.O.L. Starter 1Ph, 250V | each | 1
b) Labour charges for fixing and giving connections.
|  | Skilled Electrician | day | 0.33
|  | Helper | day | 0.33
Sunries such, as bolts, nuts and rounding off
Rate per Each
Note : Labour is Considered for 3 jobs / day
| 11.5.2(a) | Supplying and erecting D.O.L Starter 400V, 3 phase, 50Hz. enclosed with no volt coil and overload protection with necessary materials, transportation and all labour charges etc., complete suitable upto 3/4/5 HP.
a) Material
|  | D.O.L. Starter 3Ph, 415V upto 3/4/5HP | each | 1
b) Labour charges for fixing and giving connections.
|  | Skilled Electrician | day | 0.33
|  | Helper | day | 0.33
Sunries such, as bolts, nuts and rounding off
Rate per Each
Note : Labour is Considered for 3 jobs / day
| 11.5.3 | Supply and fixing of approved make semi automatic hand operated 3ph, 415V star - delta started suitable from 7.5 HP upto 15 HP motor totally enclosed with over load protection and No-volt relay etc., to complete including Transportation and all labour charges.
a) Material
|  | Semi automatic 3Ph, Induction motor with enclosure (Including of all taxes with Transportation) | each | 1
b) Labour charges for fixing and giving connections.
|  | Skilled Electrician | day | 0.5
|  | Helper | day | 0.5
Sunries such, as bolts, nuts and rounding off
Rate per Each
Note : Labour is Considered for 2 jobs / day
| 11.5.4 | Supply and fixing of approved make semi automatic hand operated 3ph, 415V star - delta started suitable upto 15 to 25 HP motor totally enclosed with over load protection and No-volt relay etc., to complete including Transportation and all labour charges.
a) Material
Deduct
|  | Cost of semi Automatic star - Delta starter | each | 1
|  | Semi automatic 3Ph, Induction motor with enclosure (Including of all taxes with Transportation) | each | 1
b) Labour charges.
|  | Skilled Electrician | day | 0.5
|  | Helper | day | 0.5
Sunries such, as bolts, nuts and rounding off
Rate per Each
Note : Labour is Considered for 2 jobs / day
| 11.5.5 | Supply and fixing of approved make automatic operated 3ph, 415V star - delta started suitable 10 to 12.5 HP automatic star delta starter motor totally enclosed with over load protection and No-volt relay to complete including Transportation and all labour charges .
a) Material
|  | Cost of semi Automatic star - Delta starter | each | 1
|  | Semi automatic 3Ph, Induction motor with enclosure (Including of all taxes with Transportation) | each | 1
b) Labour charges.
|  | Skilled Electrician | day | 0.5
|  | Helper | day | 0.5
Sunries such, as bolts, nuts and rounding off
Rate per Each
Note : Labour is Considered for 2 jobs / day
| 11.5.6 | Supply and fixing of approved make semi automatic hand operated 3ph, 415V star - delta started suitable for 15 HP fully automatic star delta motor totally enclosed with over load protection and No-volt relay to complete including Transportation and all labour charges.
a) Material
|  | Cost of semi Automatic star - Delta starter | each | 1
|  | Semi automatic 3Ph, Induction motor with enclosure (Including of all taxes with Transportation) | each | 1
b) Labour charges.
|  | Skilled Electrician | day | 0.5
|  | Helper | day | 0.5
Sunries such, as bolts, nuts and rounding off
Rate per Each
Note : Labour is Considered for 2 jobs / day
| 11.5.7 | Supply and erecting directly operated single phasing preventer connected to A.C. supply upto 45A range with guarantee to operate on single phase for one Year.
a) Material
|  | Single phase parameter upto 45A (Including all taxes and Transportation) | each | 1
b) Labour charges.
|  | Skilled Electrician | day | 0.2
|  | Helper | day | 0.2
Rate per Each
Note : Labour is Considered for 5 jobs / day
Bldngs_Elec-12 | 12 | Bus Bars
For details, Please see after Chapter 20.
Bldngs_Elec-13 | 13 | SWAGED POLES (Confirming to IS 2713 / 1980).
Bldngs_Elec-13-1 | 13.1 | Fabrication, supply and transportation of swaged poles up to site confirming to IS 2713 / 1980 specifications. The pole should be painted with primary coat of red oxide and black bituminous paint up to ground level with base plate, including cost of all materials etc., complete.
a) Material
Cost of swaged pole
Add: Labour for handling
Transportation charges, loading unloading as per Common SSR taking 250Km as average load considering fabrication point at hyd and Visakhapatnam.
Transportation charges upto 250Km Breakup.
P.No. 156 of Common SSR (Civil)
Upto 20 Km 163.80 / Tonne
|  | Upto 50 Km | 3.40 x 10
|  | Upto 80 Km | 2.80 x 50
|  | Beyond 106 Km | 2.20 x 156
|  | Loading | 15.50 / Tonne
|  | Unloading | 12.00 / Tonne
|  | Stacking | 7.00 / Tonne
Rate per Kg
D A T A F O R M . S S W A G E D P O L E S C O N F I R M I N G TO I.S : 2713 /1980
| Data No. | Specification of pole Overall length of pole. as per IS 2713 / 1980 | Planting depth in mtrs. | Length of Sections In Mtrs.
|  |  |  | Bottom | Middle | Top
| 1 | 2 3 | 4 | 5a | 5b | 5c
| 13.1.1 | 410 SP.2 7 Mtrs. | 1.25 | 4 | 1.5 | 1.5
| 13.1.2 | 410 SP.3 7 Mtrs. | 1.25 | 4 | 1.5 | 1.5
| 13.1.3 | 410 SP.5 7.5 Mtrs. | 1.25 | 4.5 | 1.5 | 1.5
| 13.1.4 | 410 SP.6 7.5 Mtrs. | 1.25 | 4.5 | 1.5 | 1.5
| 13.1.5 | 410 SP.11 8 Mtrs. | 1.5 | 4.5 | 1.75 | 1.75
| 13.1.6 | 410 SP.12 8 Mtrs. | 1.5 | 4.5 | 1.75 | 1.75
| 13.1.7 | 410 SP.26 9 Mtrs. | 1.5 | 5 | 2 | 2
| 13.1.8 | 410 SP.27 9 Mtrs. | 1.5 | 5 | 2 | 2
| 13.1.9 | 410 SP.41 10 Mtrs. | 1.8 | 5.2 | 2.4 | 2.4
| 13.1.10 | 410 SP.42 10 Mtrs. | 1.8 | 5.2 | 2.4 | 2.4
| 13.1.11 | 410 SP.50 11 Mtrs. | 1.8 | 5.6 | 2.7 | 2.7
| 13.1.12 | 410 SP.51 11 Mtrs. | 1.8 | 5.6 | 2.7 | 2.7
| 13.1.13 | 410 SP.59 12 Mtrs. | 2 | 5.8 | 3.1 | 3.1
| 13.1.14 | 410 SP.60 12 Mtrs. | 2 | 5.8 | 3.1 | 3.1
| 13.1.15 | 410 SP.73 14.5 Mtrs. | 2 | 6.5 | 4 | 4
| 13.1.16 | 410 SP.74 14.5 Mtrs. | 2 | 6.5 | 4 | 4
| 13.1.17 | 410 SP.77 16 Mtrs. | 2.3 | 7 | 4.5 | 4.5
| 13.1.18 | 410 SP.78 16 Mtrs. | 2.3 | 7 | 4.5 | 4.5
| O.D and thickness Weight of Pole in Kgs of sections |  | Weight of Base plate in Kgs. | Total weight in Kgs. | Rate/ Kg including Transportation and Fabrication | Total cost of pole
Bottom Middle Top
| 6a | 6b 6c 7 | 8 | 9 | 10 | 11
| 114.3x4.5 88.9x4.05 76.1x3.25 73 |  | 5 | 78
| 114.3x5.4 88.9x4.85 76.1x3.25 85 |  | 5 | 90
| 114.3x4.5 88.9x4.05 76.1x3.25 79 |  | 5 | 84
| 114.3x5.4 88.9x4.85 76.1x3.25 93 |  | 5 | 98
| 114.3x4.5 88.9x4.05 76.1x3.25 83 |  | 5 | 88
| 114.3x5.4 88.9x4.85 76.1x3.25 97 |  | 5 | 102
| 114.3x45 88.9x4.05 76.1x3.25 92 |  | 5 | 97
| 114.3x5.4 88.9x4.85 76.1x3.25 108 |  | 5 | 113
| 139.7x4.85 114.3x4.5 88.9x3.25 135 |  | 5 | 140
| 139.7x5.4 114.3x4.5 88.9x3.25 144 |  | 5 | 149
| 139.7x4.85 114.3x4.5 88.9x3.25 147 |  | 5 | 152
| 139.7x5.4 114.3x4.5 88.9x3.25 164 |  | 5 | 169
| 165.1x4.85 139.7x4.5 114.3x3.65 197 |  | 5 | 202
| 165.1x5.4 139.7x4.5 114.3x3.65 208 |  | 5 | 213
| 193.7x5.4 165.1x4.85 139.7x4.50 312 |  | 10 | 322
| 193.7x5.9 165.1x5.4 139.7x4.50 336 |  | 10 | 346
| 193.7x5.4 165.1x4.85 139.7x4.50 341 |  | 10 | 351
| 193.7x5.9 165.1x5.4 139.7x4.50 367 |  | 10 | 377
Bldngs_Elec-13-2 | 13.2 | Garden Posts
| 13.2.1 | Fabrication and Supply of M.S. Poles for garden posts with 'B' class 4mtrs long 60.25mm outer dia with base plate and suitable pole cap including cost and conveyance of all material including fixing of luminaire and labour charges etc., complete.
a) Material
|  | 4Mtrs 'B' Class M.S. pipe of 60.25mm dia with base plate and suitable pole cap | Kg | 24.8
Rate per Each
| 13.2.2 | Fabrication and Supply of M.S. Poles for garden posts with 'B' class 6 mtrs long 60.25mm outer dia with base plate and suitable pole cap including cost and conveyance of all material including fixing of luminaire and labour charges etc., complete.
a) Material
|  | 6Mtrs 'B' Class M.S. pipe of 60.25mm dia with base plate and suitable pole cap | Kg | 37.2
Rate per Each
Bldngs_Elec-13-3 | 13.3 | Brackets
| 13.3.1 | Supply and fixing of 50mm dia 0.5 mtrs single arm M.S. pipe bracket with sleeve and fasteners with necessary angle including painting etc., complete on existing pole including fixing of luminaire.
a) Material
|  | 0.5Mtr length 50mm 'B' class pipe. | Kg | 2.55
|  | 45cm length , 10cm dia and cap. | Kg | 5.4
|  | Painting with red oxid and enamel paint. | job | 1
b) Labour charges for fixing with Spl. T & P
|  | Skilled Electrician | day | 0.2
|  | Fitter | day | 0.2
Rate per Each
Note : Labour is Considered for 5 jobs / day
| 13.3.2 | Supply and fixing of 50mm dia 0.5 mtrs double arm M.S. pipe bracket with sleeve and fasteners with necessary angle including painting etc., complete on existing pole including fixing of luminaire
a) Material
|  | 2 x 0.5Mtr length 50mm 'B' class pipe. | Kg | 5.1
|  | 45cm length , 10cm dia and cap. | Kg | 5.4
|  | Painting with red oxid and enamel paint. | job | 1
b) Labour charges for fixing with Spl. T & P
|  | Skilled Electrician | day | 0.33
|  | Fitter | day | 0.33
Rate per Each
Note : Labour is Considered for 3 jobs / day
| 13.3.3 | Supply and fixing of 50mm dia 0.5 mtrs triple arm M.S. pipe bracket with sleeve and fasteners with necessary angle including painting etc., complete on existing pole including fixing of luminaire.
a) Material
|  | 3 x 0.5Mtr length 50mm 'B' class pipe. | Kg | 7.65
|  | 45cm length , 10cm dia and cap. | Kg | 5.4
|  | Painting with red oxid and enamel paint. | job | 1
b) Labour charges for fixing with Spl. T & P
|  | Skilled Electrician | day | 0.5
|  | Fitter | day | 0.5
Rate per Each
Note : Labour is Considered for 2 jobs / day
| 13.3.4 | Supply and fixing of 50mm dia 1 mtrs single arm M.S. pipe bracket with sleeve and fasteners with necessary angle including painting etc., complete on existing pole including fixing of luminaire
a) Material
|  | 1Mtr length 50mm 'B' class M.S pipe. | Kg | 5.1
|  | 45cm length , 10cm dia and cap. | Kg | 5.4
|  | Painting with red oxid and anamel paint. | job | 1
b) Labour charges for fixing with Spl. T & P
|  | Skilled Electrician | day | 0.2
|  | Fitter | day | 0.2
Rate per Each
Note : Labour is Considered for 5 jobs / day
| 13.3.5 | Supply and fixing of 50mm dia 1 mtrs double arm M.S. pipe bracket with sleeve and fasteners with necessary angle including painting etc., complete on existing pole including fixing of luminaire.
a) Material
|  | 2 x 1Mtr length 50mm 'B' class M.S pipe. | Kg | 10.2
|  | 45cm length , 10cm dia and cap. | Kg | 5.4
|  | Painting with red oxid and anamel paint. | job | 1
b) Labour charges for fixing with Spl. T & P
|  | Skilled Electrician | day | 0.33
|  | Helper | day | 0.33
Rate per Each
Note : Labour is Considered for 3 jobs / day
| 13.3.6 | Supply and fixing of 50mm dia 1 mtrs triple arm M.S. pipe bracket with sleeve and fasteners with necessary angle including painting etc., complete on existing pole including fixing of luminaire.
a) Material
|  | 3 x 1Mtr length 50mm 'B' class M.S pipe. | Kg | 15.3
|  | 45cm length , 10cm dia and cap. | Kg | 5.4
|  | Painting with red oxid and anamel paint. | job | 1
b) Labour charges for fixing with Spl. T & P
|  | Skilled Electrician | day | 0.5
|  | Helper | day | 0.5
Rate per Each
Note : Labour is Considered for 2 jobs / day
| 13.3.7 | Supply and fixing of 50mm dia 1.5 mtrs single arm M.S. pipe bracket with sleeve and fasteners with necessary angle including painting etc., complete on existing pole including fixing of luminaire.
a) Material
|  | 1.5 Mtr length 50mm 'B' class M.S pipe. | Kg | 7.65
|  | 45cm length , 10cm dia and cap. | Kg | 5.4
|  | Painting with red oxid and anamel paint. | job | 1
b) Labour charges for fixing with Spl. T & P
|  | Skilled Electrician | day | 0.2
|  | Helper | day | 0.2
Rate per Each
Note : Labour is Considered for 5 jobs / day
| 13.3.8 | Supply and fixing of 50mm dia 1.5 mtrs double arm M.S. pipe bracket with sleeve and fasteners with necessary angle including painting etc., complete on existing pole including fixing of luminaire.
a) Material
|  | 2 x 1.5Mtr length 50mm 'B' class M.S pipe. | Kg | 15.3
|  | 45cm length , 10cm dia and cap. | Kg | 5.4
|  | Painting with red oxid and anamel paint. | job | 1
b) Labour charges for fixing with Spl. T & P
|  | Skilled Electrician | day | 0.33
|  | Helper | day | 0.33
Rate per Each
Note : Labour is Considered for 3 jobs / day
| 13.3.9 | Supply and fixing of 50mm dia 1.5 mtrs triple arm M.S. pipe bracket with sleeve and fasteners with necessary angle including painting etc., complete on existing pole including fixing of luminaire.
a) Material
|  | 3 x 1.5Mtr length 50mm 'B' class M.S pipe. | Kg | 22.95
|  | 45cm length , 10cm dia and cap. | Kg | 5.4
|  | Painting with red oxid and anamel paint. | job | 1
b) Labour charges for fixing with Spl. T & P
|  | Skilled Electrician | day | 0.5
|  | Helper | day | 0.5
Rate per Each
Note : Labour is Considered for 2 jobs / day
| 13.3.10 | Supply and fixing of 50mm dia 1.5 mtrs curved single arm M.S. pipe bracket with sleeve and fasteners with necessary angle including painting etc., complete on existing pole including fixing of luminaire.
a) Material
|  | 1.5 Mtr length 50mm 'B' class M.S pipe. | Kg | 7.65
|  | 45cm length , 10cm dia and cap. | Kg | 5.4
|  | Painting with red oxid and anamel paint. | job | 1
b) Labour charges for fixing with Spl. T & P
|  | Skilled Electrician | day | 0.2
|  | Helper | day | 0.2
|  | For Moulding & making Suitable curve on length | job | 1
Rate per Each
Note : Labour is Considered for 5 jobs / day
| 13.3.11 | Supply and fixing of 50mm dia 1.5 mtrs curved double arm M.S. pipe bracket with sleeve and fasteners with necessary angle including painting etc., complete on existing pole including fixing of luminaire.
a) Material
|  | 2 x 1.5 Mtr length 50mm 'B' class M.S pipe. | Kg | 15.3
|  | 45cm length , 10cm dia and cap. | Kg | 5.4
|  | Painting with red oxid and anamel paint. | job | 1
b) Labour charges for fixing with Spl. T & P
|  | Skilled Electrician | day | 0.33
|  | Helper | day | 0.33
|  | For Moulding & making Suitable curve on length | job | 1
Rate per Each
Note : Labour is Considered for 3 jobs / day
| 13.3.12 | Supply and fixing of 50mm dia 1.5 mtrs curved triple arm M.S. pipe bracket with sleeve and fasteners with necessary angle including painting etc., complete on existing pole including fixing of luminaire.
a) Material
|  | 3 x 1.5 Mtr length 50mm 'B' class M.S pipe. | Kg | 22.95
|  | 45cm length , 10cm dia and cap. | Kg | 5.4
|  | Painting with red oxid and anamel paint. | job | 1
b) Labour charges for fixing with Spl. T & P
|  | Skilled Electrician | day | 0.5
|  | Helper | day | 0.5
|  | For Moulding & making Suitable curve on length | job | 1
Rate per Each
Note : Labour is Considered for 2 jobs / day
Bldngs_Elec-13-4 | 13.4 | Erection Charges for Swaged Poles
| 13.4.1 | Erection charges for 7 mtrs. to 8 mts long swaged pole including excavation of pit, coil earthing, hire charges of special T&P painting of Pole CC 1:3:6 upto ground and 1:2:4 for Couping work, including labour and transportation charges etc., complete
a) Material
|  | Pit excavation 156 Cmx 60Cmx60cm.(Civil SSR) | cum | 0.54
|  | C.C.work for pit 1:3:6 (Civil SSR) | cum | 0.54
|  | Couping 1:2:4 (Civil SSR) | cum | 0.054
|  | Painting with red oxid and enamel paint. | M | 6.2
|  | Coil earthing | each | 1
b) Labour charges
|  | Skilled Electrician | day | 0.33
|  | Helper | day | 2.67
|  | Mason | day | 0.33
Hire charges for Spl.T&P 40% on labour cost
Rate per Each
Note : Labour is Considered for 3 jobs / day
| 13.4.2(a) | Erection charges for 9 mtrs to 11 mtrs long swaged pole including excavation of pit, coil earthing, hire charges of special T&P painting of Pole CC 1:3:6 upto ground and 1:2:4 for Couping work, including labour and transportation charges etc., complete.
a) Material
|  | Pit excavation 156 Cmx 60Cmx60cm.(Civil SSR) | cum | 0.72
|  | C.C.work for pit 1:3:6 (Civil SSR) | cum | 0.72
|  | Couping 1:2:4 (Civil SSR) | cum | 0.054
|  | Painting with red oxid and enamel paint. | M | 8.35
|  | Coil earthing | each | 1
b) Labour charges
|  | Skilled Electrician | day | 0.33
|  | Helper | day | 2.67
|  | Mason | day | 0.33
Hire charges for Spl.T&P 40% on labour cost
Rate per Each
Note : Labour is Considered for 3 jobs / day
| 13.4.2(b) | Erection charges for 12 Mts to 14Mts long swaged pole including excavation of pit, coil earthing, hire charges of special T&P (Crane)painting of Pole CC 1:3:6 upto ground and 1:2:4 for Couping work, including labour and transportation charges etc., complete.
a) Material
|  | Pit excavation 2.0x1.0x1.0Mtr | cum | 2
|  | 1:3:6 CC Work | cum | 2
|  | couping 1:2:4 | cum | 0.054
|  | Painting with red oxid and alluminum paint. | M | 12
|  | Coil earthing | each | 1
b) Labour charges
|  | Skilled Electrician | day | 0.5
|  | Helper | day | 4
|  | Mason | day | 0.5
Hire charges for Spl.T&P 20% on labour cost
Rate per Each
Note : Labour is Considered for 2 jobs / day
| 13.4.3 | Erection charges for 16Mts long swaged pole including excavation of pit, coil earthing, hire charges of special T&P (Crane)painting of Pole CC 1:3:6 upto ground and 1:2:4 for Couping work, including labour and transportation charges etc., complete.
a) Material
|  | Pit excavation 2.30x1.0x1.0Mtr | cum | 2.3
|  | 1:3:6 CC Work | cum | 2.3
|  | couping 1:2:4 | cum | 0.054
|  | Painting with red oxid and alluminum paint. | M | 14
|  | Coil earthing | each | 1
b) Labour charges
|  | Skilled Electrician | day | 0.5
|  | Helper | day | 4
|  | Mason | day | 0.5
Hire charges for Spl.T&P 20% on labour cost
Rate per Each
Note : Labour is Considered for 2 jobs / day
| 13.4.4 | Erection charges for 7to 9Mts long swaged pole on bridge kerb portion ( R.C.C. work with V.C.C. M.15 concrete with 3 Nos 25x6 mm MS Special clamps bolts with nuts and locking nuts etc.including cost and con veyance of all material and all labour charges etc. complete with painting.
a) Material
|  | Painting with red oxid and enamel paint. | M | 6.2
|  | Coil earthing | each | 1
|  | 3 Nos, 25 x 6 mm MS Special Clamps of 1 M Length each @ 1.18 Kg | Kg | 3.54
|  | VCC M 15 Concrete 0.5 x 0.3 x 0.9 | cum | 0.135
b) Labour charges
|  | Skilled Electrician | day | 0.33
|  | Helper | day | 2.67
|  | Mason | day | 0.33
|  | Fanrication of clamps | kgs | 3.54
Hire charges for Spl.T&P 20% on labour cost
Rate per Each
Note : Labour is Considered for 3 jobs / day
| 13.4.5 | Erection charges for 4 Mtrs. Long MS / GI Garden post including excavation of pit, concreting 1:3:6 and painting including cost and conveyance of all materials including fixing of luminaire and labour charges etc., complete.
a) Material
|  | Pit excavation (0.4x0.4x1.0 mtr) | cum | 0.16
|  | Painting with red oxide and enamel paint. | M | 2.5
|  | 1:3:6 C.C work. | cum | 0.16
b) Labour charges
|  | Mason | day | 0.2
|  | Helper | day | 0.4
Rate per Each
Note : Labour is Considered for 5 jobs / day
| 13.4.6 | Erection charges for 6Mtrs. Long MS / GI Garden post including excavation of pit, concreting 1:3:6 and painting including cost and conveyance of all materials including fixing of luminaire and labour charges etc., complete.
a) Material
|  | Pit excavation ( 0.45x0.45x1.25) | cum | 0.25
|  | 1: 3: 6 C.C. work | cum | 0.25
|  | Painting with red oxide and enamel paint | M | 4.75
b) Labour charges
|  | Mason | day | 0.2
|  | Helper | day | 0.4
Rate per Each
Note : Labour is Considered for 5 jobs / day
| 13.4.7 | Fabrication, supply and fixing of luminaire carriage, made with 50mm dia M.S. 'B' class pipe, moulded to 6 feet dia ring wheel, and 40mm dia M.S support pieces on 4 sides inside the wheel and necessary size of M.S pole cap for fixing the ring wheel on the 156mm dia M.S. pole for fixing floodlight and gear box with suitable nut & bolts and painted with Red Oxide and Aluminium paint including cost & conveyance of all materials etc., complete.
a) Material
|  | 50mm 'B' class MS pipe of 5.7mts (1Mt=5.106Kgs) | Kg | 29.07
|  | 40mm 'B' glass pipe MS pipe of 3.6Mtr (1Mt=3.61Kgs) | Kg | 13
|  | 200mm MS pipe for pole cap.C-Class (heavy) 0.3Mts (1Mt=31Kgs) | Kg | 13
|  | Special bolts and nuts 6" length. | each | 12
|  | Painting with red oxide and enamel paint etc., | Job | 1
b) Labour charges
|  | Fitter | day | 0.5
|  | Helper | day | 4
Rate per Each
Note : Labour is Considered for 2 jobs / day
Bldngs_Elec-13-5 | 13.5 | Accessories
| 13.5.1 | Supply and fixing of 300mm x 260mm x 140mm No.16 gauge CRCA sheet box with hinged door and locking arrangements and din channel for fixing 2Nos MCBs duly powder coated with matching colour of poles including fixing with necessary arrangments etc., complete.
a) Material
|  | 300x260x140mm 16 guage CRCA box finished of item(as per 14.1.2) | sqm | 0.35
Sundries as rounding off
Rate per Each
| 13.5.2 | Supply and fixing of 300mm x 180mm x 140mm No.16 gauge CRCA sheet box with hinged door and locking arrangements and din channel for fixing 2Nos MCBs duly powder coated with matching colour of poles including fixing with necessary arrangments etc., complete.
a) Material
|  | 300x180x140mm 16 guage CRCA sheet box as per 14.1.2 | sqm | 0.29
Sundries as rounding off
Rate per Each
| 13.5.3 | Supply and fixing of 1 No.10A SP MCB in existing M.S. box with Din channel, 4way 63A connector including cost & conveyance of all materials and labour charges etc., complete.
a) Material
|  | 10A SP MCB | each | 1
|  | 4Way connector. | each | 1
b) Labour charges
|  | Skilled Electrician | day | 0.066
Rate per Each
Note : Labour is Considered for 15 jobs / day
| 13.5.4 | Supply and fixing of 2 Nos 10A SP MCBs in existing M.S box with Din channel, 4way 63A connector including cost & conveyance of all materials and labour charges etc., complete.
a) Material
|  | 10A SP MCB | each | 2
|  | 4Way connector. | each | 1
b) Labour charges
|  | Skilled Electrician | day | 0.066
Sundries such as screws, tape
Rate per Each
Bldngs_Elec-14 | 14 | CONTROL PANEL AND METERING EQUIPMENT
Bldngs_Elec-14-1 | 14.1 | CONTROL PANEL
| 14.1.1 | Supply, Transportation, fabrication and erection of following guage CRCA sheet steel enclosure for power control cubicle panel / boxes etc., including cutting, bending drilling, welding and reveting etc., complete with cleaning with 7 tank process and painting with powder coating including cost and conveyance of all materials and labour charges.
| 1) | 14 SWG CRCA sheet steel enclosure
a) Material
|  | 14 SWG (2mm) CRCA sheet - 1 sft (Wt of 8 x 4 feet sheet, 50Kg) | kg | 1.56
|  | Transportation charges on Material cost |  | 2%
|  | Fabrication including cutting, bending, drilling and Dust proof arrnagments etc., |  | 30%
|  | Cleaning of cubicals in seven tank process |  | 40%
|  | Painting with powder coating. |  | 40%
|  | Erection charges |  | 30%
Sundires such as hardware etc.,
Rate per sft
Rate per sqm
| 14.1.2 | 16 SWG CRCA sheet steel enclosure
a) Material
|  | 16 SWG (2mm) CRCA sheet - 1sft (Wt of 8 x 4 feet sheet, 39Kg) | kg | 1.218
|  | Transportation charges |  | 2%
|  | Fabrication including cutting, bending, drilling and Dust proof arrnagments etc., |  | 30%
|  | Cleaning of cubicals in seven tank process |  | 40%
|  | Painting with powder coating. |  | 40%
|  | Erection charges |  | 30%
Sundires such as hardware etc.,
Rate per sft
Rate per sqm
| 14.1.3 | 18 SWG CRCA sheet steel enclosure
a) Material
|  | 18 SWG (2mm) CRCA sheet - 1 sft (Wt of 8 x 4 feet sheet, 30Kg) | kg | 0.937
|  | Transportation charges |  | 2%
|  | Fabrication including cutting, bending, drilling and Dust proof arrnagments etc., |  | 30%
|  | Cleaning of cubicals in seven tank process |  | 40%
|  | Painting with powder coating. |  | 40%
|  | Erection charges |  | 30%
Sundires such as hardware etc.,
Rate per sft
Rate per sqm
Bldngs_Elec-14-2 | 14.2 | METERING EQUIPMENT
| 14.2.1 | Supply and erection of 0-500V volt meter of size 96x96mm on exisiting box / panel board including connections etc., complete.
a) Material
|  | 0-500 Voltmeter Analog / Degital inclusive of all Taxes. | each | 1
b) Labour charges for fixing & Connections
|  | Skilled Electrician | day | 0.2
Rate per Each
Note : Labour is Considered for 5 jobs / day
| 14.2.2 | Supply and erection of 0-100 / 200 / 400 / 600 /1000 - 5A CT Ammeter of size 96x96mm on existing box / panel board including connections etc., complete.
a) Material
|  | 96 x 96mm size Ammeter Analog / Degital inclusive of all Taxes | each | 1
b) Labour charges for fixing and connections.
|  | Skilled Electrician | day | 0.2
Rate per Each
| 14.2.3 | Supply and erection of frequency meter of size 96x96mm on existing box / panel board including connections etc., complete.
a) Material
|  | Frequency meter Analog / Degital inclusive of all Taxes. | each | 1
b) Labour charges for fixing and connections.
|  | Skilled Electrician | day | 0.2
Rate per Each
| 14.2.4 | Supply and erection of power factor meter, 3 phase, 4 wire balanced or unbalanced load 5A, 415V of size 96x96mm on existing box / panel board including connections etc., complete.
a) Material
|  | Power Factor meter Analog / Degital inclusive of all Taxes. | each | 1
b) Labour charges for fixing and connections.
|  | Skilled Electrician | day | 0.2
Rate per Each
| 14.2.5 | Supply and erection of L.T. 3phase multifunction energy meter with 3 lines LCD display of size 96x96mm for measuring all the parameters (voltage / Current / Power / frequency / power factor / KW / KWH / KVAR/ KVARH) on existing box panel board including connections etc., complete.
a) Material
|  | L.T. 3 Ph. Multifunction energy meter Analog / Degital inclusive of all Taxes. | each | 1
b) Labour charges for fixing and connections.
|  | Skilled Electrician | day | 0.33
Rate per Each
Note : Labour is Considered for 3 jobs / day
| 14.2.6 | Supply and erection of selector switch for voltmeter / Ammeter on the existing box / panel including connections etc., complete.
a) Material
|  | Selector switch for Ammeter / Voltmeter. | each | 1
b) Labour charges for fixing and connections.
|  | Skilled Electrician | day | 0.2
Rate per Each
Note : Labour is Considered for 5 jobs / day
| 14.2.7 | Supply and erection of LED indicator lamps on the existing box / panel board.
a) Material
|  | LED indicator lamp Analog | each | 1
b) Labour charges for fixing and connections.
|  | Skilled Electrician | day | 0.1
Rate per Each
Note : Labour is Considered for 10 jobs / day
| 14.2.8 | Supply and erection of LT current transformer with bar primary 100/5A to 1000 / 5A ratio in the existing box / panel including connections etc., complete.
a) Material
|  | L.T. C.T with bar primary 100 / 5A to 1000 / 5A | each | 1
b) Labour charges for fixing and connections.
|  | Skilled Electrician | day | 0.1
Rate per Each
Note : Labour is Considered for 10 jobs / day
| 14.2.9 | Supply and fixing of single phase energy Meter,240V AC,50 HZ as per IS13010 with 2.5-5 /5-10/10-20 Amps range with 200% over load capacity complete with connections etc., complete on the existing board.
a) Material
|  | cost of single phase energy meter | each | 1
b) Labour charges for fixing and connections.
|  | Skilled Electrician | day | 0.33
sunderies
Rate per Each
Note : Labour is Considered for 3 jobs / day
| 14.2.10 | Supply and fixing of three phase energy Meter,415V AC,50 HZ as per IS13010 with 2.5-5 /5-10/10-20 Amps range with 200% over load capacity complete with connections etc., complete on the existing board.
a) Material
|  | Cost of three phase energy meter | each | 1
b) Labour charges for fixing and connections.
|  | Skilled Electrician | day | 0.33
sunderies
Rate per Each
Note : Labour is Considered for 3 jobs / day
Bldngs_Elec-15 | 15 | CABLES / CABLE GLANDS / LUGS
Bldngs_Elec-15-1 | 15.3 | CABLE GLANDS
| 15.3.1 | Supply and Fixing of heavy duty flange type brass cable glands for 2 to 4 core, 2.5 Sq.mm to 6 Sq.mm PVC armoured cable with brass washers complete.
a) Material
|  | Brass cable gland for 2-4 core, 2.5 Sqmm to 6 Sq.mm armoured cable | each | 1
b) Labour charges for fixing glands.
|  | Semi skilled Electrician | day | 0.066
Sundireis and Rounding off
Rate per Each
Note : Labour is Considered for 15 jobs / day
| 15.3.2 | Supply and Fixing of heavy duty flange type brass cable glands for 2 to 4 core, 10 Sq.mm PVC armoured cable with brass washers complete.
a) Material
|  | Brass cable gland for 2-4 core, 10 Sqmm armoured cable | each | 1
b) Labour charges for fixing glands.
|  | Semi skilled Electrician | day | 0.066
Sundireis and Rounding off
Rate per Each
Note : Labour is Considered for 15 jobs / day
| 15.3.3 | Supply and Fixing of heavy duty flange type brass cable glands for 4 core, 16 Sq.mm / 3.5 core 25Sq.mm PVC armoured cable with brass washers complete.
a) Material
|  | Brass cable gland suitabtle for 4core 16 Sq.mm / 3.5 core 25 Sq.mm armoured cable | each | 1
b) Labour charges for fixing glands.
|  | Skilled Electrician | day | 0.066
Sundireis and Rounding off
Rate per Each
| 15.3.4 | Supply and Fixing of heavy duty flange type brass cable glands for 3.5 core, 35 Sq.mm / 3.0 core 50Sq.mm PVC armoured cable with brass washers complete.
a) Material
|  | Brass cable gland suitabtle for 3.5core 35 Sq.mm / 3 core 50 Sq.mm armoured cable | each | 1
b) Labour charges for fixing glands.
|  | Skilled Electrician | day | 0.066
Sundireis and Rounding off
Rate per Each
Note : Labour is Considered for 15 jobs / day
| 15.3.5 | Supply and Fixing of heavy duty flange type brass cable glands for 3.5 core, 50 Sq.mm PVC armoured cable with brass washers complete.
a) Material
|  | Brass cable gland suitabtle for 3.5core 50 Sq.mm armoured cable | each | 1
b) Labour charges for fixing glands.
|  | Skilled Electrician | day | 0.066
Sundireis and Rounding off
Rate per Each
Note : Labour is Considered for 15 jobs / day
| 15.3.6 | Supply and Fixing of heavy duty flange type brass cable glands for 3.5 core, 70 Sq.mm PVC armoured cable with brass washers complete.
a) Material
|  | Brass cable gland suitabtle for 3.5core 70Sq.mm armoured cable | each | 1
b) Labour charges for fixing glands.
|  | Skilled Electrician | day | 0.066
|  | Helper | day | 0.066
Sundireis and Rounding off
Rate per Each
Note : Labour is Considered for 15 jobs / day
| 15.3.7 | Supply and Fixing of heavy duty flange type brass cable glands for 3.5 core, 95 Sq.mm PVC armoured cable with brass washers complete.
a) Material
|  | Brass cable gland suitabtle for 3.5core 95 Sq.mm armoured cable | each | 1
b) Labour charges for fixing glands.
|  | Skilled Electrician | day | 0.066
|  | Helper | day | 0.066
Sundireis and Rounding off
Rate per Each
Note : Labour is Considered for 15 jobs / day
| 15.3.8 | Supply and Fixing of heavy duty flange type brass cable glands for 3.5 core, 120 Sq.mm PVC armoured cable with brass washers complete.
a) Material
|  | Brass cable gland suitabtle for 3.5core 120 Sq.mm armoured cable | each | 1
b) Labour charges for fixing glands.
|  | Skilled Electrician | day | 0.066
|  | Helper | day | 0.066
Sundireis and Rounding off
Rate per Each
Note : Labour is Considered for 15 jobs / day
| 15.3.9 | Supply and Fixing of heavy duty flange type brass cable glands for 3.5 core, 150 Sq.mm PVC armoured cable with brass washers complete.
a) Material
|  | Brass cable gland suitabtle for 3.5core 150 Sq.mm armoured cable | each | 1
b) Labour charges for fixing glands.
|  | Skilled Electrician | day | 0.083
|  | Helper | day | 0.083
Sundireis and Rounding off
Rate per Each
Note : Labour is Considered for 12 jobs / day
| 15.3.10 | Supply and Fixing of heavy duty flange type brass cable glands for 3.5 core, 185 Sq.mm PVC armoured cable with brass washers complete.
a) Material
|  | Brass cable gland suitabtle for 3.5core 185 Sq.mm armoured cable | each | 1
b) Labour charges for fixing glands.
|  | Skilled Electrician | day | 0.083
|  | Helper | day | 0.083
Sundireis and Rounding off
Rate per Each
Note : Labour is Considered for 12 jobs / day
| 15.3.11 | Supply and Fixing of heavy duty flange type brass cable glands for 3.5 core, 240 Sq.mm PVC armoured cable with brass washers complete.
a) Material
|  | Brass cable gland suitabtle for 3.5core 240 Sq.mm armoured cable | each | 1
b) Labour charges for fixing glands.
|  | Skilled Electrician | day | 0.083
|  | Helper | day | 0.083
Sundireis and Rounding off
Rate per Each
Note : Labour is Considered for 12 jobs / day
| 15.3.12 | Supply and Fixing of heavy duty flange type brass cable glands for 3.5 core, 300 Sq.mm PVC armoured cable with brass washers complete.
a) Material
|  | Brass cable gland suitabtle for 3.5core 300 Sq.mm armoured cable | each | 1
b) Labour charges for fixing glands.
|  | Skilled Electrician | day | 0.1
|  | Helper | day | 0.1
Sundries, such as insulated tape.
Rate per Each
Note : Labour is Considered for 10 jobs / day
| 15.3.13 | Supply and Fixing of heavy duty flange type brass cable glands for 3.5 core, 400 Sq.mm PVC armoured cable with brass washers complete.
a) Material
|  | Brass cable gland suitabtle for 3.5core 400 Sq.mm armoured cable | each | 1
b) Labour charges for fixing glands.
|  | Skilled Electrician | day | 0.1
|  | Helper | day | 0.1
Sundries, such as insulated tape.
Rate per Each
Note : Labour is Considered for 10 jobs / day
Bldngs_Elec-15-2 | 15.4 | CABLE LUGS:
| 15.4.1 | Supply and fixing of crimping type copper lugs confirming to I.S specifications for cable upto 16 Sq.mm including nuts and bolts with connections.
a) Material
|  | Copper Lugs upto 16 Sq.mm. | each | 1
b) Labour charges for crimping
|  | Semi Skilled Electrician | day | 0.01
|  | Helper | day | 0.01
Sundries such as bolts and nuts.
Rate per Each
Note : Labour is Considered for 100 jobs / day
| 15.4.2 | Supply and fixing of crimping type copper lugs confirming to I.S specifications for cable of 25 Sq.mm including nuts and bolts with connections.
a) Material
|  | Copper Lugs upto 25 Sq.mm. | each | 1
b) Labour charges for crimping
|  | Semi Skilled Electrician | day | 0.01
|  | Helper | day | 0.01
Sundries such as bolts and nuts.
Rate per Each
Note : Labour is Considered for 100 jobs / day
| 15.4.3 | Supply and fixing of crimping type copper lugs confirming to I.S specifications for cable of 35 Sq.mm including nuts and bolts with connections.
a) Material
|  | Copper Lugs up to 35 sqmm | each | 1
b) Labour charges for crimping
|  | Semi Skilled Electrician | day | 0.013
|  | Helper | day | 0.013
Sundries such as bolts and nuts.
Rate per Each
Note : Labour is Considered for 75 jobs / day
| 15.4.4 | Supply and fixing of crimping type copper lugs confirming to I.S specifications for cable of 50 Sq.mm including nuts and bolts with connections.
a) Material
|  | Copper Lugs upto 50 Sq.mm. | each | 1
b) Labour charges for crimping
|  | Semi Skilled Electrician | day | 0.013
|  | Helper | day | 0.013
Sundries such as bolts and nuts.
Rate per Each
Note : Labour is Considered for 75 jobs / day
| 15.4.5 | Supply and fixing of crimping type copper lugs confirming to I.S specifications for cable of 70Sq.mm including nuts and bolts with connections.
a) Material
|  | Copper Lugs upto 70 Sq.mm. | each | 1
b) Labour charges for crimping
|  | Semi Skilled Electrician | day | 0.013
|  | Helper | day | 0.013
Sundries such as bolts and nuts.
Rate per Each
Note : Labour is Considered for 75 jobs / day
| 15.4.6 | Supply and fixing of crimping type copper lugs confirming to I.S specifications for cable of 95 Sq.mm including nuts and bolts with connections.
a) Material
|  | Copper Lugs up to 95 sqmm | each | 1
b) Labour charges for crimping
|  | Semi Skilled Electrician | day | 0.016
|  | Helper | day | 0.016
Sundries such as bolts and nuts.
Rate per Each
Note : Labour is Considered for 60 jobs / day
| 15.4.7 | Supply and fixing of crimping type copper lugs confirming to I.S specifications for cable of 120 Sq.mm including nuts and bolts with connections.
a) Material
|  | Copper Lugs up to 120 sqmm | each | 1
b) Labour charges for crimping
|  | Semi Skilled Electrician | day | 0.02
|  | Helper | day | 0.02
Sundries such as bolts and nuts.
Rate per Each
Note : Labour is Considered for 50 jobs / day
| 15.4.8 | Supply and fixing of crimping type copper lugs confirming to I.S specifications for cable of 150 Sq.mm including nuts and bolts with connections.
a) Material
|  | Copper Lugs up to 150 sqmm | each | 1
b) Labour charges for crimping
|  | Semi Skilled Electrician | day | 0.033
|  | Helper | day | 0.033
Sundries such as bolts and nuts.
Rate per Each
Note : Labour is Considered for 30 jobs / day
| 15.4.9 | Supply and fixing of crimping type copper lugs confirming to I.S specifications for cable of 185 Sq.mm including nuts and bolts with connections.
a) Material
|  | Copper Lugs up to 185 sqmm | each | 1
b) Labour charges for crimping
|  | Semi Skilled Electrician | day | 0.033
|  | Helper | day | 0.033
Sundries such as bolts and nuts.
Rate per Each
Note : Labour is Considered for 30 jobs / day
| 15.4.11 | Supply and fixing of crimping type copper lugs confirming to I.S specifications for cable of 240 Sq.mm including nuts and bolts with connections.
a) Material
|  | Copper Lugs up to 240 sqmm | each | 1
b) Labour charges for crimping
|  | Semi Skilled Electrician | day | 0.04
|  | Helper | day | 0.04
Sundries such as bolts and nuts.
Rate per Each
Note : Labour is Considered for 25 jobs / day
| 15.4.12 | Supply and fixing of crimping type copper lugs confirming to I.S specifications for cable of 300 Sq.mm including nuts and bolts with connections.
a) Material
|  | Copper Lugs up to 300 sqmm | each | 1
b) Labour charges for crimping
|  | Semi Skilled Electrician | day | 0.05
|  | Helper | day | 0.05
Sundries such as bolts and nuts.
Rate per Each
Note : Labour is Considered for 20 jobs / day
| 15.4.13 | Supply and fixing of crimping type copper lugs confirming to I.S specifications for cable of 400 Sq.mm including nuts and bolts with connections.
a) Material
|  | Copper Lugs up to 400 sqmm | each | 1
b) Labour charges for crimping
|  | Semi Skilled Electrician | day | 0.062
|  | Helper | day | 0.062
Sundries such as bolts and nuts.
Rate per Each
Note : Labour is Considered for 16 jobs / day
| 15.4.14 | Supply and fixing of crimping type Aluminium lugs confirming to I.S specifications for cables upto 16 Sq.mm including nuts and bolts with connections.
a) Material
|  | Aluminium Lugs up to 16 sqmm | each | 1
b) Labour charges for crimping
|  | Semi Skilled Electrician | day | 0.01
|  | Helper | day | 0.01
Sundries such as bolts and nuts.
Rate per Each
Note : Labour is Considered for 100 jobs / day
| 15.4.15 | Supply and fixing of crimping type Aluminium lugs confirming to I.S specifications for cable of 25 Sq.mm including nuts and bolts with connections.
a) Material
|  | Aluminium Lugs up to 25 sqmm | each | 1
b) Labour charges for crimping
|  | Semi Skilled Electrician | day | 0.01
|  | Helper | day | 0.01
Sundries such as bolts and nuts.
Rate per Each
Note : Labour is Considered for 100 jobs / day
| 15.4.16 | Supply and fixing of crimping type Aluminium lugs confirming to I.S specifications for cable of 35 Sq.mm including nuts and bolts with connections.
a) Material
|  | Aluminium Lugs up to 35 sqmm | each | 1
b) Labour charges for crimping
|  | Semi Skilled Electrician | day | 0.013
|  | Helper | day | 0.013
Sundries such as bolts and nuts.
Rate per Each
Note : Labour is Considered for 75 jobs / day
| 15.4.17 | Supply and fixing of crimping type Aluminium lugs confirming to I.S specifications for cable of 50 Sq.mm including nuts and bolts with connections.
a) Material
|  | Aluminium Lugs up to 50 sqmm | each | 1
b) Labour charges for crimping
|  | Semi Skilled Electrician | day | 0.013
|  | Helper | day | 0.013
Sundries such as bolts and nuts.
Rate per Each
Note : Labour is Considered for 75 jobs / day
| 15.4.18 | Supply and fixing of crimping type aluminium lugs confirming to I.S specifications for cable of 70 Sq.mm including nuts and bolts with connections.
a) Material
|  | Aluminium Lugs up to 70 sqmm | each | 1
b) Labour charges for crimping
|  | Semi Skilled Electrician | day | 0.013
|  | Helper | day | 0.013
Sundries such as bolts and nuts.
Rate per Each
Note : Labour is Considered for 75 jobs / day
| 15.4.19 | Supply and fixing of crimping type aluminium lugs confirming to I.S specifications for cable of 95 Sq.mm including nuts and bolts with connections.
a) Material
|  | Aluminium Lugs up to 95 sqmm | each | 1
b) Labour charges for crimping
|  | Semi Skilled Electrician | day | 0.016
|  | Helper | day | 0.016
Sundries such as bolts and nuts.
Rate per Each
Note : Labour is Considered for 60 jobs / day
| 15.4.20 | Supply and fixing of crimping type aluminium lugs confirming to I.S specifications for cable of 120 Sq.mm including nuts and bolts with connections.
a) Material
|  | Aluminium Lugs up to 120 sqmm | each | 1
b) Labour charges for crimping
|  | Semi Skilled Electrician | day | 0.02
|  | Helper | day | 0.02
Sundries such as bolts and nuts.
Rate per Each
Note : Labour is Considered for 50 jobs / day
| 15.4.21 | Supply and fixing of crimping type aluminium lugs confirming to I.S specifications for cable of 150 Sq.mm including nuts and bolts with connections.
a) Material
|  | Aluminium Lugs up to 150 sqmm | each | 1
b) Labour charges for crimping
|  | Semi Skilled Electrician | day | 0.04
|  | Helper | day | 0.04
Sundries such as bolts and nuts.
Rate per Each
Note : Labour is Considered for 25 jobs / day
| 15.4.22 | Supply and fixing of crimping type aluminium lugs confirming to I.S specifications for cable of 185 Sq.mm including nuts and bolts with connections.
a) Material
|  | Aluminium Lugs up to 185 sqmm | each | 1
b) Labour charges for crimping
|  | Semi Skilled Electrician | day | 0.04
|  | Helper | day | 0.04
Sundries such as bolts and nuts.
Rate per Each
Note : Labour is Considered for 25 jobs / day
| 15.4.24 | Supply and fixing of crimping type aluminium lugs confirming to I.S specifications for cable of 240 Sq.mm including nuts and bolts with connections.
a) Material
|  | Aluminium Lugs up to 240 sqmm | each | 1
b) Labour charges for crimping
|  | Semi Skilled Electrician | day | 0.04
|  | Helper | day | 0.04
Sundries such as bolts and nuts.
Rate per Each
Note : Labour is Considered for 25 jobs / day
| 15.4.25 | Supply and fixing of crimping type aluminium lugs confirming to I.S specifications for cable of 300 Sq.mm including nuts and bolts with connections.
a) Material
|  | Aluminium Lugs up to 300 sqmm | each | 1
b) Labour charges for crimping
|  | Semi Skilled Electrician | day | 0.05
|  | Helper | day | 0.05
Sundries such as bolts and nuts.
Rate per Each
Note : Labour is Considered for 20 jobs / day
| 15.4.26 | Supply and fixing of crimping type aluminium lugs confirming to I.S specifications for cable of 400 Sq.mm including nuts and bolts with connections.
a) Material
|  | Aluminium Lugs up to 400 sqmm | each | 1
b) Labour charges for crimping
|  | Semi Skilled Electrician | day | 0.062
|  | Helper | day | 0.062
Sundries such as bolts and nuts.
Rate per Each
Note : Labour is Considered for 16 jobs / day
Bldngs_Elec-15-3 | 15.5 | CABLE JOINTS
| 15.5.1 | Providing and erecting epoxy staight through joint out door / indoor for L.T, PVC Armoured cable 1100V grade complete with ferrule, bushings, accessories and suitable clamps duly erected and connected to the supply for the following multi core cables including cost and conveyance of materials and all labour charges etc., complete.
| (a) | 2.5 Sq.mm to 16 Sq.mm
a) Material
|  | Epoxy straight joint 2.5 to 16 Sq.mm with accessories | each | 1
b) Labour charges
|  | Skilled Electrician | day | 0.5
|  | Helper | day | 0.5
Sundries
Rate per Each
Note : Labour is Considered for 2 jobs / day
| (b) | 25 Sq.mm to 50 Sq.mm
a) Material
|  | Epoxy straight joint 25 to 50 Sq.mm with accessories | each | 1
b) Labour charges
|  | Semi Skilled Electrician | day | 0.5
|  | Helper | day | 0.5
Sundries
Rate per Each
Note : Labour is Considered for 2 jobs / day
| (c ) | 70 Sq.mm to 95 Sq.mm
a) Material
|  | Epoxy straight joint 70 to 95 Sq.mm with accessories | each | 1
b) Labour charges
|  | Semi Skilled Electrician | day | 0.5
|  | Helper | day | 0.5
Sundries
Rate per Each
Note : Labour is Considered for 2 jobs / day
| (d) | 120 Sq.mm to 185 Sq.mm
a) Material
|  | Epoxy straight joint 120 to 185 Sq.mm with accessories | each | 1
b) Labour charges
|  | Semi Skilled Electrician | day | 0.5
|  | Helper | day | 0.5
Sundries
Rate per Each
Note : Labour is Considered for 2 jobs / day
| (e) | 240 Sq.mm
a) Material
|  | Epoxy straight joint 240 Sq.mm with accessories | each | 1
b) Labour charges
|  | Skilled Electrician | day | 1
|  | Helper | day | 1
Sundries
Rate per Each
| (f) | 300 Sq.mm
a) Material
|  | Epoxy straight joint 300 Sq.mm with accessories | each | 1
b) Labour charges
|  | Skilled Electrician | day | 1
|  | Helper | day | 1
Sundries
Rate per Each
| (g) | 400 Sq.mm
a) Material
|  | Epoxy straight joint 400 Sq.mm with accessories | each | 1
b) Labour charges
|  | Skilled Electrician | day | 1
|  | Helper | day | 1
Sundries
Rate per Each
Bldngs_Elec-15-4 | 15.6 | Labour Charges Laying of Cable including cost of all Materials other than Cable
| 15.6.1 | Earth work excavation of Trench in hard ground soil, laying of U.G cables upto 50 Sq,mm on sand cushion covering the cable with bricks and back filling of Trench duly providing route indicator embedded in C.C including cost and conveyance of materials and labour charges etc., complete.
a) Material
|  | Excavation of earth 100 x 0.3 X 0.9 m | cum | 27
|  | Cost of bricks (Civil SSR) | 1000 Nos | 0.92
|  | Cost of sand (Civil SSR) | cum | 6
|  | Cement (Civil SSR) | Kg | 25
|  | Cost of cable route indicator | each | 12
|  | Transportation charges of bricks and sand | LS
b) Labour charges for laying cable.
|  | Man Mazdoor for spreading the sand and back filling the excavated soil. | each | 2.5
|  | Skilled Electrician | day | 1
|  | Helper | day | 2
|  | Man Mazdoor for concreting and embedding of cable way indicators | day | 2
Sundires and Rounding off
Rate per 100mts
Note : Labour Charges Considered for 100 Mts / day
| 15.6.2 | Earth work excavation of Trench in hard ground soil, laying of U.G cables from 70 sqmm to 400 Sq,mm on sand cushion covering the cable with bricks and back filling of Trench duly providing route indicator embedded in C.C including cost and conveyance of materials and labour charges etc., complete.
a) Material
|  | Excavation of earth 100 x 0.3 X 0.9 m | cum | 27
|  | Cost of bricks (Civil SSR) | 1000 Nos | 0.92
|  | Cost of sand (Civil SSR) | cum | 6
|  | Cement (Civil SSR) | Kg | 25
|  | Cost of cable route indicator | each | 12
|  | Transportation charges of bricks and sand | LS
b) Labour charges for laying cable.
|  | Man Mazdoor for spreading the sand and back filling the excavated soil. | each | 2.5
|  | Skilled Electrician | day | 1.6
|  | Helper | day | 3.3
|  | Man Mazdoor for concreting and embedding of cable way indicators | day | 2
Sundires and Rounding off
Rate per 60mts
Note :1. Labour Charges Considered for 60 Mts / day
2. Cables shall be at a depth of not less than 600 mm in a trench. Sand filling shall be provided at the bottom of trench before laying the cable. Bricks shall be provided on either side of the laid cable. Sand filling shall be done to cover the cable laid. bricks shall be provided onthe Top. earth filling shall be done. cable identificaiton tags to be provided at every 8 mtrs length of cable laid.
3. Only the cost of cables may be added for finished item.
| 15.6.3 | Labour charges for run of U.G cable on wall / existing pipe with necessary fixing arrangments such as saddles, clamps,wooden separators etc., (as directed by departmental official) with No.10 SWG G.I wire for eath connections for the cables.
a) Material
|  | Wooden separators | each | 200
|  | saddles of required size | 100 nos | 2
|  | 12mm screws | 100 nos | 4
|  | No.10 SWG GI wire | kg | 7
b) Labour charges
|  | Skilled Electrician | day | 1
|  | Helper | day | 4
Sundires such as Cement, Sand etc.,
Rate per Each
Note : Labour Charges Considered for 100 Mts / day
| 15.6.4 | Supply and laying of one number double walled corrugated (DWC) HDPE pipe of following sizes having corrugation on the outer wall and plain surface inner wall confirming to IS : 14930 Part - I and II complete with necessary HDPE fittings for protection of 1.1 KV grade U.G cable directly in ground at a depth of 60Cms including excavation and refilling the trench as required.
a) 50mm outer dia nominal size
b) 78mm outer dia nominal size
c) 90mm outer dia nominal size
d) 120mm outer dia nominal size
a) Material
|  | Double wall corrugated HDPE pipe confirming to IS : 14930. | RM | 6
|  | Snap-fit coupler | each | 1
|  | Excavation of earth work & Refilling for a size of 1.0x0.3x0.6Mtr. | cum | 0.18
Rate per Metre
Bldngs_Elec-16 | 16 | TEMPORARY ILLUMINATION
data shown seperately at the end.
Bldngs_Elec-17 | 17 | GENERATORS AND TRANSFORMERS
Bldngs_Elec-17-1 |  | Supply, Transportation, erection and commissioning of following specifications of D.G. Set consists of Engine and alternator which are directly coupled by means of flexible cooping with guard and mounted on a common base plate of Robust construction and complete with control panel having IP 53 protection.
| A | Alternator : KIRLOSKAR / STAMFORD / CROMPTON on D.G.S & D approved make. The alternator of the output rating shall be 1 Ph / 3 Ph, 240V / 415V, 50 Hz., A.C., 0.8 P.f lagging at 1500 RPM. The alternator is self excited, self regulated, screen protected drip proof and shall confirm to IS : 13364 of 1992 with regulation of + 5% from no load to full load. degree of protections shall be IP 21.
| B | Diesel Engine : KIRLOSKAR / GREAVES / CUMMINS / ASHOK LEY LAND or DGS&D approved. Diesel Engine start, developing suitable BHP output at 1500 RPM with class A2 Governing so as to enable the alternator to give required KVA continuous output at 0.8 P.F. lagging at NTP conditions. the Diesel Engine will be capable of providing 10% O/L for 1 Hr for every 11 HRs of continuous running at full load. The Diesel Engine shall confirm to IS 10001 or IS 10002.
| C | Control Panel : Control Panel shall be fabricated with 16 SWG CRCA sheet steel. The control panel shall be totally enclosed, dust and vermin proof, floor mounted / wall mounted type and shall be comprising the following instruments and component.
1. Voltmeter with selector switch 2. Ammeter with Selector Switch
3. MCCB / MCB incomer of suitable rating 4. P.F. Meter and frequency Meter
5. Indication Lamp Set 6. KWH Meter of required rating
7. Instrument and control fuses.
ACOUSTIC ENCLOSURE
Supply & providing & installation of acoustic enclosure (sound proof enclosure cum container) for the above Genset with the following specification.
Construction : The panel of acoustic enclosure shall consists of self supporting frame work put together with help of fasteners, which is for assembling and dismantling. The vertical and Horizontal structure 8is to be fabricated with 14/16 SWG CRCA sheet and should be fixed on heavy duty MS Channel which will form the base frame of the acoustic enclosure. the paneling of ht container is to be carried out using 18 SWG CRCA sheets. the enclosure should be self supporting type and does not require any grouting or separate foundation. But it should be the independent of the DG set and to placed around the DG set. The frame work shall also have provision for fitting hinged / sliding doors to open either sides of the enclosure.
| 17.1 | Generating Sets
| 17.1.3 (a) | Supply, Transportation, erection of 3 Ph Air-Cooled 20KVA, D.G.Set with alternator, Diesel Engine, Control panel etc., as per specifications mentioned above.
a) Material
|  | 20KVA Air Cooled, 3Ph, 451V, 50Hz., D.G.Set. | each | 1
|  | Erection and commissioning charges @ 10% of the cost of the set. |  | 10%
|  | Transportation at 2% on unit cost |  | 2%
Sundires and Rounding off
Rate per Each
| 17.1.3 (b) | Supply, Transportation, erection of 3 Ph Air-Cooled 20KVA, D.G.Set with alternator, Diesel Engine, Control panel etc., with acoustic enclosure as per specifications mentioned above.
a) Material
|  | 20KVA Air Cooled, 3Ph, 451V, 50Hz., D.G.Set | each | 1
|  | cost of acoustic enclosure | each | 1
Erection and commissioning charges :
|  | the cost of the DG set. |  | 10%
|  | cost of acoustic enclosure |  | 5%
|  | Transportation at 2% on unit cost |  | 2%
Sundires and Rounding off
Rate per Each
| 17.1.3 (c) | Supply, Transportation, erection of 3 Ph Air-Cooled 25KVA, D.G.Set with alternator, Diesel Engine, Control panel etc., as per specifications mentioned above.
a) Material
|  | 3Ph, 415V, 50Hz., 25 KVA Air Cooled D.G.Set | each | 1
|  | Erection and commissioning charges @ 10% of the cost of the set. |  | 10%
|  | Transportation at 2% on unit cost |  | 2%
Sundires and Rounding off
Rate per Each
| 17.1.3 (d) | Supply, Transportation , erection of 3 Ph Air-Cooled 25KVA, D.G.Set with alternator, Diesel Engine, Control panel etc., with acoustic enclosure as per specifications mentioned above.
a) Material
|  | 3Ph, 415V, 50Hz., 25 KVA Air Cooled D.G.Set | each | 1
|  | Cost of Acoustic enclosure | each | 1
Erection and commissioning charges :
|  | the cost of the DG set. |  | 10%
|  | cost of acoustic enclosure |  | 5%
|  | Transportation at 2% on unit cost |  | 2%
Sundires and Rounding off
Rate per Each
| 17.1.3 (e) | Supply, Transportation, erection of 3 Ph Air-Cooled 40KVA, D.G.Set with alternator, Diesel Engine, Control panel etc., as per specifications mentioned above.
a) Material
|  | 40KVA, 3Ph,415V,D.G.Set | each | 1
|  | Erection and commissioning charges @ 10% of the cost of the set. |  | 10%
|  | Transportation at 2% on unit cost |  | 2%
Sundires and Rounding off
Rate per Each
| 17.1.3 (f) | Supply, Transportation, erection of 3 Ph Air-Cooled 40KVA, D.G.Set with alternator, Diesel Engine, Control panel etc., with acoustic enclosure as per specifications mentioned above.
a) Material
|  | 40KVA, 3Ph,415V,D.G.Set | each | 1
|  | Cost of Acoustic enclosure | each | 1
Erection and commissioning charges :
|  | the cost of the DG set. |  | 10%
|  | cost of acoustic enclosure |  | 5%
|  | Transportation at 2% |  | 2%
Sundires and Rounding off
Rate per Each
| 17.1.3 (g) | Supply, Transportation , erection of 3 Phase Water cooled / Air Cooled 63KVA, D.G.Set with alternator, Diesel Engine, Control panel etc., as per specifications mentioned above.
a) Material
|  | 63KVA, 3Ph, 415V, D.G Set | each | 1
|  | Erection and commissioning charges @ 10% of the cost of the set. |  | 10%
|  | Transportation at 2% |  | 2%
Sundires and Rounding off
Rate per Each
| 17.1.3 (h) | Supply, Transportation , erection of 3 Phase Water Cooled / Air-Cooled 63KVA, D.G.Set with alternator, Diesel Engine, Control panel etc., with acoustic enclosure as per specifications mentioned above.
a) Material
|  | 63KVA, 3Ph, 415V, D.G Set | each | 1
|  | Cost of Acoustic enclosure | each | 1
Erection and commissioning charges :
|  | the cost of the DG set. |  | 10%
|  | cost of acoustic enclosure |  | 5%
|  | Transportation at 2% |  | 2%
Sundires and Rounding off
Rate per Each
| 17.1.3 (i) | Supply, Transportation , erection of 3 Phase Water cooled 125 KVA, D.G.Set with alternator, Diesel Engine, Control panel etc., as per specifications mentioned above.
a) Material
|  | 125KVA, Water Cooled, 3Ph, 415V D.G.Set. | each | 1
|  | Erection and commissioning charges @ 10% of the cost of the set. |  | 10%
|  | Transportation at 2% |  | 2%
Sundires and Rounding off
Rate per Each
| 17.1.3 (j) | Supply, Transportation, erection of 3 Phase Water-Cooled 125KVA, D.G.Set with alternator, Diesel Engine, Control panel etc., with acoustic enclosure as per specifications mentioned above.
a) Material
|  | 125KVA, Water Cooled, 3Ph, 415V D.G.Set. | each | 1
|  | Cost of Acoustic enclosure | each | 1
Erection and commissioning charges :
|  | the cost of the DG set. |  | 10%
|  | cost of acoustic enclosure |  | 5%
|  | Transportation at 2% |  | 2%
Sundires and Rounding off
Rate per Each
Bldngs_Elec-17-2 | 17.2 | Transformers
| 17.2.1 | Supply, transportation, erection and commissioning of following specifications of 3 Phase, 50 Hz., Oil immersed and naturally cooled, out door / Indoor type copper wound transformer connected delta on H.V. side and star on L.V side with additional neutral brought out on load side, rating 11000 / 433 volts with HV tapping + 2.5% cotinuously rated for full load and temparature rise not exceeding 450 C by thermometer in oil and 500 C by the resistance of the winding after continuous run on full load rating complete with the following standard mounting.
| (a) | 63 KVA, 3Ph, aluminium wound Tansformer, CSP type (Core Self Protection)
a) Material
|  | 63KVA Aluminium wound CSP type Transformer | each | 1
|  | Transportation including loading and unloading |  | 2%
|  | (b) Labour charges for erection and commissioning. |  | 10%
Rate per Each
| (b) | 100 KVA, 3Ph, aluminium wound Tansformer, CSP type
a) Material
|  | 100 KVA Aluminium wound CSP type Transformer | each | 1
|  | Transportation including loading and unloading |  | 2%
|  | (b) Labour charges for erection and commissioning. |  | 10%
Rate per Each
| (c ) | 100 KVA, 3Ph, copper wound Tansformer
a) Material
|  | 100 KVA Copper wound Transformer | each | 1
|  | Transportation including loading and unloading |  | 2%
|  | (b) Labour charges for erection and commissioning. |  | 10%
Rate per Each
| (d ) | 160 KVA, 3Ph, copper wound Tansformer
a) Material
|  | 160 KVA Copper wound Transformer | each | 1
|  | Transportation including loading and unloading |  | 2%
|  | (b) Labour charges for erection and commissioning. |  | 10%
Rate per Each
| (e) | 200 KVA, 3Ph, copper wound Tansformer
a) Material
|  | 200 KVA Copper wound Transformer | each | 1
|  | Transportation including loading and unloading |  | 2%
|  | (b) Labour charges for erection and commissioning. |  | 10%
Rate per Each
| (f) | 250 KVA, 3Ph, copper wound Tansformer
a) Material
|  | 250 KVA Copper wound Transformer | each | 1
|  | Transportation including loading and unloading |  | 2%
|  | (b) Labour charges for erection and commissioning. |  | 10%
Rate per Each
| (g) | 315 KVA, 3Ph, copper wound Tansformer
a) Material
|  | 315 KVA Copper wound Transformer | each | 1
|  | Transportation including loading and unloading |  | 2%
|  | (b) Labour charges for erection and commissioning. |  | 10%
Rate per Each
| (h) | 500 KVA, 3Ph, copper wound Tansformer
a) Material
|  | 500 KVA Copper wound Transformer | each | 1
|  | Transportation including loading and unloading |  | 2%
|  | (b) Labour charges for erection and commissioning. |  | 10%
Rate per Each
| (i) | 630 KVA, 3Ph, copper wound Tansformer
a) Material
|  | 630 KVA Copper wound Transformer | each | 1
|  | Transportation including loading and unloading |  | 2%
|  | (b) Labour charges for erection and commissioning. |  | 10%
Rate per Each
| (j) | 1000 KVA, 3Ph, copper wound Tansformer
a) Material
|  | 1000 KVA Copper wound Transformer | each | 1
|  | Transportation including loading and unloading |  | 2%
|  | (b) Labour charges for erection and commissioning. |  | 10%
Rate per Each
Bldngs_Elec-17-3 | 17.3 | CIRCUIT BREAKER
| 17.3.7 | Supply and errecting Air circuit Breaker (ACB) manually operated non drawout type with 6 way secondary isolating contacts necessary micro switches for over load and short circuit indicator, door interlocking, shunt release, under voltage release as well as 10%-20% earth fault release suitable for operational voltage 415V, 630A, erected in position on provided panel boards in an approved manner with necessary material complete
a) Material
|  | 630A, 415V Fixed type 3 pole ACB | each | 1
|  | Shunt release | each | 1
|  | U/V release | each | 1
|  | Earth fault release | each | 1
|  | Transportation @ 2% on Unit Cost |  | 2%
|  | b) Labour charges for installation @ 5% |  | 5%
Rate per Each
| 17.3.8 | Supply and errecting Air circuit Breaker (ACB) manually operated non drawout type with 6 way secondary isolating contacts necessary micro switches for over load and short circuit indicator, door interlocking, shunt release, under voltage release as well as 10%-20% earth fault release suitable for operational voltage 415V, 800A, erected in position on provided panel boards in an approved manner with necessary material complete.
a) Material
|  | 800A, 415V Fixed type 3 pole ACB | each | 1
|  | Shunt release Coil. | each | 1
|  | U/V release Coil. | each | 1
|  | Earth fault release | each | 1
|  | Transportation @ 2% on Unit Cost |  | 2%
|  | b) Labour charges for installation @ 5% |  | 5%
Rate per Each
| 17.3.9 | Supply and errecting Air circuit Breaker (ACB) manually operated non drawout type with 6 way secondary isolating contacts necessary micro switches for over load and short circuit indicator, door interlocking, shunt release, under voltage release as well as 10%-20% earth fault release suitable for operational voltage 415V, 1000A, erected in position on provided panel boards in an approved manner with necessary material complete.
a) Material
|  | 1000A, 415V, Fixed type 3 pole ACB. | each | 1
|  | Shunt release | each | 1
|  | U/V release | each | 1
|  | Earth fault release | each | 1
|  | Transportation @ 2% on Unit Cost |  | 2%
|  | b) Labour charges for installation @ 5% |  | 5%
Rate per Each
Bldngs_Elec-17-4 | 17.4 | SUB - STATION EQUIPMENT
| 17.4.1 | Supply and fixing printed instructions chart both in English and Telugu and duly framed with front glass for treatment of person suffering from Electric shock.
a) Material
|  | Printed insturction chart both of size 0.9 x 0.6 M in English and Telugu. | each | 1
|  | Towards making wooden frame with front glass including cost of material and labour on unti cost of Item 1. |  | 150%
Rate per Each
| 17.4.2 | Supply of pair of rubber hand gloves suitable for working 11/22 KV supply.
a) Material
|  | Rubber hand gloves suitable for working on 11/22 KV supply | each | 1
Rate per Each Pair
| 17.4.3 | Supply of 11KV, ISI, approved rubber mat of thickness, required length and breadth.
a) Material
|  | 6mm thick, ISI make Rubber mat suitable for working on 11/22 KV | each | 1
Sundries and rounding off
Rate per sqmt
| 17.4.4 | Supply of standard 18"x12"x8" first aid box with all standard contents.
a) Material
|  | 18" x 12" x 8" size First Aid box. | each | 1
|  | Set of Cotton, band aid cloth Antiseptic cream etc., | set | 1
Rate per Each
| 17.4.5 | Supply of G.I sheet bucket of round bottom of 13 Ltrs. Capacity with printed letters and filled with sand and arranged to existing stand or hook.
a) Material
|  | 13 Ltrs. Capacity G.I. bucket. | each | 1
|  | Painting with 2 coats of red color enamell paint on out side. | sqm | 0.5
|  | Cost of sand | cum | 0.13
Sundires for printing letter etc.,
Rate per Each
| 17.4.6 | Supply of Tranformer oil tested and having good resistance to high electric stress di-electric strength 50KV, low viscocity, low pour point, high flash point and excellent thermal properties for efficient heat transfer and cooling as per IS 335-1972.
a) Material
|  | Transformer Oil having Dielectric strength of 50 KV | L | 1
Sundries and rounding off
Rate per Lt
| 17.4.7 | Providing floor mounting stand for keeping 4Nos of bucket 1500mm length, 900mm height made out of 40x40x6mm angle iron welded with 4 hooks and duly painted with one coat of red lead and two coats of enamel paint.
a) Material
|  | 1500mm length, 900mm height Floor mounting stand fabricated with 40x40x6mm angle iron welded with 4 Nos Hooks. (1Mtr = 3.5Kg) (5x3.5Kgs = 17.5Kgs) | kg | 17.5
|  | Fabrication cost of hooks including painting (on cost of material) |  | 50%
Sundries and rounding off
Rate per Each
| 17.4.8 | Supply and erecting ABC Powder (stored pressure type) fire extinguisher 5kg conforming to IS 2171-85 with necessary clamps made from 50x6mm MS flat with nuts & bolts grouted in wall complete.
a) Material
|  | ABC Powder Stored pressure type fire extengensher of 5 Kg capacity . | each | 1
|  | 50 x6mm M.S Apl. Clamps with bolt & nut. | each | 1
(b) Labour charges for erection.
|  | Helper | day | 0.2
Sundires and Rounding off
Rate per Each
Note : Labour is considered for 5 jobs / day
| 17.4.9 | Supply and erecting ABC Powder (stored pressure type) fire extinguisher 10kg conforming to IS 2171-85 with necessary clamps made from 50x6mm MS flat with nuts & bolts grouted in wall complete.
a) Material
|  | ABC Powder Stored pressure type fire extengensher of 10 Kg capacity . | each | 1
|  | 50 x6mm M.S Apl. Clamps with bolt & nut. | each | 1
(b) Labour charges for erection.
|  | Helper | day | 0.2
Sundires and Rounding off
Rate per Each
Note : Labour is considered for 5 jobs / day
| 17.4.10 | Supply and erecting fencing of section having size 2450 mm in height from ground level and 1200mm width by using angle iron size 50x50x6mm erected in CC foundation 15x15x40cms deep. The section of the frame shall be fitted with flat iron supports of size 25x6mm on top, bottom and middle and chain link jali of 8 SWG G.I to the angle iron at every distance of 30 cms by iron studs complete duly painted with one coat of red oxide and two coats of aluminium paint.
a) Material
|  | 50x50x6mm Angle Iron (1 Mt. = 4.37 Kg) 4.8 m Length | kg | 20.97
|  | 25x6mm M.S Flat (1 Mt. 1.18 Kg) 3.6 M length | kg | 4.25
|  | Chain link Mesh (Civil SSR) | sqm | 2.4
|  | Fabrication of Frame with angles, Flat and chain link mesh | kg | 25.22
|  | C.C.Work M 15 using 20 mm metal (15 x 15 x 40) x 2 As per Civil SSR | cum | 0.018
|  | Painting with one coat of red oxide and two coat of alluminium paint. | sqm | 5.88
Sundires and Rounding off
Rate per Each
| 17.4.11 | Supply and erecting 50x50x6mm angle iron as corner support to be fixed away from the fence support fixed at the middle of the fencing frame and the other side in CC foundation of 15x15x40 cms complete duly painted with one coat of red oxide and two coats of aluminium paint.
a) Material
|  | 50x50x6mm Angle. (1 mt. 4.37 Kg) 2m Length | kg | 8.74
|  | C.C.Work M 15 using 20 mm metal (15 x 15 x 40) x 2 As per Civil SSR | cum | 0.018
|  | Painting with one coat of red oxide and two coats of Aluminium paint (on cost of Item 1) |  | 10%
Sundires and Rounding off
Rate per Each
| 17.4.12 | Supply and erecting double leaf hinged door each 150cms width x 185cms height using 38.1 mm dia B grade ISI marked G.I pipe from all four sides with necessary bends with cross supports of angle iron 40 x 40 x 6mm with the door leaf covered with chain link mesh of No. 8 SWG G.I wire with necessary flat iron covering all around frame. The door shall have heavy latches, and side channels of 100x50x5mm locking arrangement with lock of medium size with duplicate keys, the fencing completely erected with anti corrosive red oxide paint and two coats of prescribed enamel paint / silver paint. The channel iron of size 100x50mm x 2.5Mtr. length shall be provided and erected at both sides of gate with C.C work
a) Material
|  | 38.1mm dia B Class G.I pipe. (1.85 x 4 Nos + 1.5x 4Nos = 13.4 Mt or say 14 Mtrs.) ( civil SSR) | RM | 14
|  | 25x6mm M.S. Flat (1.18 Kgs / Mt) 17 M length | kg | 20.06
|  | 1000x50mm Channle (1mt = 8.74 Kg) 5 M length | kg | 43.7
|  | 4 Nos x 2.38M Length, 40 x 40 x 6 mm M.S. Angle Iron ( 1 Mtr = 3.5 Kg) 9.52 M length | kg | 33.32
|  | Steel Aldrop with bolts and Nuts. | each | 1
|  | Chain link mesh of 8 SWg G.I (Civil SSR) | sqm | 5.55
|  | Medium size lock and Key | each | 1
|  | Fabrication charges including welding etc., complete. | kg | 118
|  | Painting Charges | sqm
|  | b) Labour charges for erection including cost of hinges on items 1-6. |  | 5%
Sundireis and Rounding off
Rate per Each
Bldngs_Elec-17-5 | 17.5 | SUB-STATION MAINTENANCE
| 17.5.1 (a) | Filteration of transformer oil as per ISS for removal of moisture, carbon slurry etc. by means of circulating oil through vaccum pump from heating elements and filters to withstand the dielectric strength of the oil above 40KV beyond one minute tested in oil testing Kit. |  |  |  |  | Data shall be arrived based on observed Data
On site.
a) Material
Labour charges for filterations at site
Rate per Each
| 17.5.1 (b) | Filteration of transformer oil as per ISS for removal of moisture, carbon slurry etc. by means of circulating oil through vaccum pump from heating elements and filters to withstand the dielectric strength of the oil above 40KV beyond one minute tested in oil testing Kit. |  |  |  |  | Data shall be arrived based on observed Data
At Factory.
a) Material
Labour charges for filterations at site
Rate per Each
| 17.5.3 | Carryout routine maintenance, servicing and testing of 630A to 1000A L.T.ACB by cleaning fixed contacts, moving contacts and arcchutes including servicing and putting the ACB in perfect working condition after detting all relay and ON, OFF mechanism etc.
a) Material
Removing the existing ACB and servicing and testing of 630A to 1000A L.T.ACB.
Clearing of fixed contacts, moving contacts and arcchutes
Refix the ACB inposition and testing and commissioning charges.
b) Labour charges for entire job
|  | Skilled Electrician | day | 3
|  | Semi Skilled Electrician | day | 3
|  | Helper | day | 6
Sundries and Rounding
Rate per Each
Note :Job requires 3 days. Keeping this labour arrived.
| 17.5.4 | Carryout routine maintenance and servicing of LT.Cubical panel board having approximately 15 to 22 Nos of switches by cleaning with power blower and servicing the contacts, tightning the connection of incoming and outgoing cables, and clicking the operating mechanism for smooth functioning of switches and putting them in smooth working condition.
a) Material
Removing all the doors of switches, busbar chamber and back doors.
Clearing by using power blower.
Tightening all the terminations and cleaning and servicing the contacts of switches.
b) Labour charges for entire job
|  | Skilled Electrician | day | 2
|  | Semi Skilled Electrician | day | 1
|  | Helper | day | 2
Sundries and Rounding
Rate per Each
Note :Job requires 3 days. Keeping this labour arrived.
Bldngs_Elec-17-6 | 17.6 | PROTECTIVE GEAR
| 17.6.1 | Supply and erecting approved make 11KV, 5KA metal oxide lightning arrestors suitable for 11 KV supply with necessary materials on existing cross arm.
a) Material
|  | Cost of 11 KV 5KA metal oxide lighting arrester. | each | 1
b) Labour charges for erection.
|  | Skilled Electrician | day | 0.33
|  | Helper | day | 0.33
Sundries
Rate per Each
Note : Labour is considered for 3 jobs / day
| 17.6.3 | Supply and erecting porcelain disc type insulator suitable for 11KV line with suitable hardware on existing cross arms.
a) Material
|  | Cost of porcelain disc type insulator suitable for 11 KV | each | 1
b) Labour charges for erection.
|  | Skilled Electrician | day | 0.125
|  | Helper | day | 0.25
Sundries
Rate per Each
Note : Labour is considered for 8 jobs / day
| 17.6.5 | Supply and erecting porcelain pin type insulator suitable for 11KV line with suitable hardware on existing cross arms.
a) Material
|  | Cost of porcelain pin type insulator suitable for 11 KV | each | 1
b) Labour charges for erection.
|  | Skilled Electrician | day | 0.125
|  | Helper | day | 0.25
Sundries
Rate per Each
Note : Labour is considered for 8 jobs / day
| 17.6.6 | Supply and erecting porcelain post type insulator suitable for 11KV line with suitable hardware on existing cross arms.
a) Material
|  | Cost of porcelain post type insulator suitable for 11 KV | each | 1
b) Labour charges for erection.
|  | Skilled Electrician | day | 0.125
|  | Helper | day | 0.25
Sundries
Rate per Each
Note : Labour is considered for 8 jobs / day
| 17.6.8 | Supply and fixing of lightning protective system conforming to IS : 2309 with all standard accessories such as metal globe finials on the top of the builiding with 25.4 mm dia 3.0 mtrs. Length of 'B' class G.I pipe etc., complete without down conductors and earthing
a) Material
|  | Lightning protective system with all standard accessories such as metallic globe, finials etc., | each | 1
|  | 25.4 mm B Class GI Pipe, ISI Mark | M | 3
b) Labour charges
i) for fixing the System on G.I pipe.
ii) for fixing on top of the building with C.C work / Clamping arrangement.
|  | Skilled Electrician | day | 1
|  | Helper | day | 1
Sundries and Rounding off
Rate per Each
| 17.6.10 | Supply and erecting approved made 11KV, 400A A.B switch with all standard accessories etc., complelte with cost and conveyance of all materials and labour charges.
a) Material
|  | Cost of 11KV, 400A A.B switch wth all standard accessories. | each | 1
b) Labour charges for erection.
|  | Skilled Electrician | day | 1
|  | Semi Skilled Electrician | day | 1
|  | Helper | day | 1
Sundries and Rounding off
Rate per Each
| 17.6.11 | Supply and erecting approved made 11KV, 200A A.B switch with all standard accessories etc., complelte with cost and conveyance of all materials and labour charges.
a) Material
|  | Cost of 11KV, 200A A.B switch wth all standard accessories. | each | 1
b) Labour charges for erection.
|  | Skilled Electrician | day | 1
|  | Semi Skilled Electrician | day | 1
|  | Helper | day | 1
Sundries and Rounding off
Rate per Each
| 17.6.12 | Supply and erecting approved made 11KV, 200A (Tilting) A.B switch with all standard accessories etc., complelte with cost and conveyance of all materials and labour charges.
a) Material
|  | Cost of 11kV, 200A (Tilting) A.B switch wth all standard accessories. | each | 1
b) Labour charges for erection.
|  | Skilled Electrician | day | 1
|  | Semi Skilled Electrician | day | 1
|  | Helper | day | 1
Sundries and Rounding off
Rate per Each
| 17.6.13 | Supply and erecting 11KV, H.G (Horn Gap) fuse set including all standard accessories etc., complete with cost and conveyance of all materials and labour charges.
a) Material
|  | Cost of 11KV, H.G. fuse set wth all standard accessories. | each | 1
b) Labour charges for erection.
|  | Skilled Electrician | day | 1
|  | Helper | day | 1
Sundries and Rounding off
Rate per Each
| 17.6.14 | Supply and erecting of bank of metalised polypropylene condensors with the standard capacities of 2,3,5,7,10,12.5 and 15 KVAR units for PF correction for operation on 3 phase 50 Cycles 400 / 440V (+10%) with externally discharging resistances, earthig terminals etc., complete.
a) Material
|  | Cost of MPP capacitor operation on 3 Ph. 415V. | Kvar | 1
b) Labour charges for erection.
|  | Skilled Electrician | day | 0.04
|  | Helper | day | 0.08
Sundries and Rounding off
Rate per Kvar
Note : Labour considered for 25 jobs / day
| 17.6.15 | Supply and erecting of bank of mixdielectric condensors with the standard capacities of 2,3,5,7,10,12.5 and 15 KVAR units for PF correction for operation on 3 phase 50 cycles 400/440V (+10%) with externally discharging resistances, earthing terminals etc., complete.
a) Material
|  | Cost of of mixed Dielectric capacitor operation on 3 Ph. 415V. | Kvar | 1
b) Labour charges for erection.
|  | Skilled Electrician | day | 0.04
|  | Helper | day | 0.08
Sundries and Rounding off
Rate per Kvar
Note : Labour considered for 25 jobs / day
Bldngs_Elec-18 | 18 | Repairs to Motors and Rewinding
Datas of 11.6.1 to 11.6.4 are hold good and be adopted.
Bldngs_Elec-18-1 | 18.1.1 | Rewinding the motor of the table / pedestal / cabin fan of all types, and makes and overhauling including minor repairs, testing for the original speed and consumption with guarantee for one year including tansporation from site and back.
a) Material
|  | Copper enamelled winding wire of fine quality. | kg | 0.3
|  | Labour charges towards removing unserviceable winding wire and cleaning. (on cost of winding wire) |  | 50%
|  | Labour charges towards rewinding the coils complete with connections etc., complete.(on cost of winding wire) |  | 100%
|  | Sundries such as sleeves cotton tape, minolex paper, solution etc., with transportion charges. |  | 40%
|  | Less cost towards old winding wire | kg | 0.3
Rate per Each
| 18.1.2 | Rewinding the motor of the ceiling fan of 1200mm / 1400mm of all types and makes and over hauling including minor repairs and testing for original speed and consumption
a) Material
|  | 35 / 36 Copper enamelled winding wire of fine quality. | kg | 0.2
|  | Labour charges towards removing unserviceable winding wire and cleaning. (on cost of winding wire) |  | 50%
|  | Labour charges towards rewinding the coils complete with connections etc., complete.(on cost of winding wire) |  | 100%
|  | Sundries such as sleeves cotton tape, minolex paper, solution etc., with transportion charges. |  | 40%
|  | Less cost towards old winding wire | kg | 0.2
Rate per Each
| 18.1.3 | Rewinding the motor of the exhaust fan of light duty 225/300mm of 900/1400 RPM of all types and makes and over hauling including minor repairs and testing for original speed and consumption
a) Material
|  | 23 / 24 / 28 Copper enamelled winding wire of fine quality. | kg | 0.05
|  | Labour charges towards removing unserviceable winding wire and cleaning. (on cost of winding wire) |  | 50%
|  | Labour charges towards rewinding the coils complete with connections etc., complete.(on cost of winding wire) |  | 100%
|  | Sundries such as sleeves cotton tape, minolex paper, solution etc., with transportion charges. |  | 40%
|  | Less cost towards old winding wire | kg | 0.05
Rate per Each
| 18.1.4 | Rewinding the motor of the exhaust fan of heavy duty 375mm of 900/1400 RPM of all types and makes and over hauling including minor repairs and testing for original speed and consumption
a) Material
|  | 23 / 24 / 28 Copper enamelled winding wire of fine quality. | kg | 0.45
|  | Labour charges towards removing unserviceable winding wire and cleaning. (on cost of winding wire) |  | 50%
|  | Labour charges towards rewinding the coils complete with connections etc., complete.(on cost of winding wire) |  | 100%
|  | Sundries such as sleeves cotton tape, minolex paper, solution etc., with transportion charges. |  | 40%
|  | Less cost towards old winding wire | kg | 0.45
Rate per Each
| 18.1.5 | Rewinding of electric motor upto 1 HP single phase upto 1400 RPM of all types and makes with copper wire, overhauling with minor repairs, testing for the original speed and no load consumption .
a) Material
|  | Suitable guage copper winding wire fine quality | kg | 2.7
|  | Labour charges towards removing of old unserviceable winding wire.(on cost of winding wire) |  | 5%
|  | Labour charges towards rewinding copper coils complete with connections.(on cost of winding wire) |  | 12%
|  | Sundries such as sleeves, cotton tape, minolex paper solution etc., with transportation. |  | 2%
|  | Less cost towards old winding wire | kg | 2.7
Rate per Each
| 18.1.6 | Rewinding of electric motor 2 HP single phase 1400 RPM of all types and makes with copper wire, overhauling with minor repairs, testing for the original speed and no load consumption.
a) Material
|  | Suitable guage copper winding wire fine quality | kg | 3.2
|  | Labour charges towards removing of old unserviceable winding wire.(on cost of winding wire) |  | 5%
|  | Labour charges towards rewinding copper coils complete with connections.(on cost of winding wire) |  | 12%
|  | Sundries such as sleeves, cotton tape, minolex paper solution etc., with transportation. |  | 2%
|  | Less cost towards old winding wire | kg | 3.2
Rate per Each
| 18.1.7 | Rewinding of electric motor 3 HP three phase 1400 RPM of all types and makes with copper wire, overhauling with minor repairs, testing for the original speed and no load consumption .
a) Material
|  | Suitable guage copper winding wire fine quality | kg | 4.5
|  | Labour charges towards removing of old unserviceable winding wire.(on cost of winding wire) |  | 5%
|  | Labour charges towards rewinding copper coils complete with connections.(on cost of winding wire) |  | 12%
|  | Sundries such as sleeves, cotton tape, minolex paper solution etc., with transportation. |  | 2%
|  | Less cost towards old winding wire | kg | 4.5
Rate per Each
| 18.1.8 | Rewinding of electric motor 5 HP three phase 1400 RPM of all types and makes with copper wire, overhauling with minor repairs, testing for the original speed and no load consumption .
a) Material
|  | Suitable guage copper winding wire fine quality | kg | 5.7
|  | Labour charges towards removing of old unserviceable winding wire.(on cost of winding wire) |  | 5%
|  | Labour charges towards rewinding copper coils complete with connections.(on cost of winding wire) |  | 12%
|  | Sundries such as sleeves, cotton tape, minolex paper solution etc., with transportation. |  | 2%
|  | Less cost towards old winding wire | kg | 5.7
Rate per Each
| 18.1.9 | Rewinding of electric motor 7.5 HP three phase 1400 RPM of all types and makes with copper wire, overhauling with minor repairs, testing for the original speed and no load consumption .
a) Material
|  | Suitable guage copper winding wire fine quality | kg | 6.5
|  | Labour charges towards removing of old unserviceable winding wire.(on cost of winding wire) |  | 5%
|  | Labour charges towards rewinding copper coils complete with connections.(on cost of winding wire) |  | 12%
|  | Sundries such as sleeves, cotton tape, minolex paper solution etc., with transportation. |  | 2%
|  | Less cost towards old winding wire | kg | 6.5
Rate per Each
| 18.1.10 | Rewinding of electric motor 10 HP three phase 1400 RPM of all types and makes with copper wire, overhauling with minor repairs, testing for the original speed and no load consumption .
a) Material
|  | Suitable guage copper winding wire fine quality | kg | 10
|  | Labour charges towards removing of old unserviceable winding wire.(on cost of winding wire) |  | 5%
|  | Labour charges towards rewinding copper coils complete with connections.(on cost of winding wire) |  | 12%
|  | Sundries such as sleeves, cotton tape, minolex paper solution etc., with transportation. |  | 2%
|  | Less cost towards old winding wire | kg | 10
Rate per Each
| 18.1.11 | Rewinding of electric motor 12.50 HP three phase 1400 RPM of all types and makes with copper wire, overhauling with minor repairs, testing for the original speed and no load consumption .
a) Material
|  | Suitable guage copper winding wire fine quality | kg | 12
|  | Labour charges towards removing of old unserviceable winding wire.(on cost of winding wire) |  | 5%
|  | Labour charges towards rewinding copper coils complete with connections.(on cost of winding wire) |  | 12%
|  | Sundries such as sleeves, cotton tape, minolex paper solution etc., with transportation. |  | 2%
|  | Less cost towards old winding wire | kg | 12
Rate per Each
| 18.1.12 | Rewinding of electric motor 15 HP three phase 1400 RPM of all types and makes with copper wire, overhauling with minor repairs, testing for the original speed and no load consumption .
a) Material
|  | Suitable guage copper winding wire fine quality | kg | 15
|  | Labour charges towards removing of old unserviceable winding wire.(on cost of winding wire) |  | 5%
|  | Labour charges towards rewinding copper coils complete with connections.(on cost of winding wire) |  | 12%
|  | Sundries such as sleeves, cotton tape, minolex paper solution etc., with transportation. |  | 2%
|  | Less cost towards old winding wire | kg | 15
Rate per Each
| 18.1.13 | Rewinding of electric motor 20 HP three phase 1400 RPM of all types and makes with copper wire, overhauling with minor repairs, testing for the original speed and no load consumption.
a) Material
|  | Suitable guage copper winding wire fine quality | kg | 18
|  | Labour charges towards removing of old unserviceable winding wire.(on cost of winding wire) |  | 5%
|  | Labour charges towards rewinding copper coils complete with connections.(on cost of winding wire) |  | 12%
|  | Sundries such as sleeves, cotton tape, minolex paper solution etc., with transportation. |  | 2%
|  | Less cost towards old winding wire | kg | 18
Rate per Each
| 18.1.14 | Rewinding of submersible motor upto 15 HP three phase of all types and makes with copper wire, overhauling with minor repairs, testing for the original speed and no load consumption .
a) Material
|  | PVC insulated copper winding wire of suitable guage. | kg | 18
|  | Labour charges towards removing of old unserviceable winding wire.(on cost of winding wire) |  | 10%
|  | Labour charges towards rewinding copper coils complete with connections.(on cost of winding wire) |  | 15%
|  | Sundries such as sleeves, cotton tape, minolex paper solution etc., with transportation. |  | 5%
|  | Less cost for winding wire | kg | 18
Rate per Each
Bldngs_Elec-18-2 | 18.2 | Bearings
| 18.2.1 | Replacing the existing bearing of approved make for electric motor single phase / 3 phase AC upto 1 HP of all types with due alignment of the shaft and tested.
a) Material
|  | Ball Bearings suitable for 1 HP Motor inclusive of taxes | each | 1
|  | Labour charges for removing the existing unserviceable bearing and fixing the new ball bearing with special T&P. (on cost of Ball Bearing) |  | 50%
Transportation and Rounding off
Rate per Each
| 18.2.2 | Replacing the existing bearing of approved make for electric motor single phase / 3 phase AC upto 2 to 3 HP of all types with due alignment of the shaft and tested.
a) Material
|  | Ball Bearings suitable for 2 to 3 HP Motor inclusive of taxes | each | 1
|  | Labour charges for removing the existing unserviceable bearing and fixing the new ball bearing with special T&P. (on cost of Ball Bearing) |  | 50%
Transportation and Rounding off
Rate per Each
| 18.2.3 | Replacing the existing bearing of approved make for electric motor single phase / 3 phase AC upto 5 to 7.5 HP of all types with due alignment of the shaft and tested.
a) Material
|  | Ball Bearings suitable for 5 to 7.5 HP Motor inclusive of taxes | each | 1
|  | Labour charges for removing the existing unserviceable bearing and fixing the new ball bearing with special T&P. (on cost of Ball Bearing) |  | 50%
Transportation and Rounding off
Rate per Each
| 18.2.4 | Replacing the existing bearing of approved make for electric motor single phase / 3 phase AC upto 10 to 12.5 HP of all types with due alignment of the shaft and tested.
a) Material
|  | Ball Bearings suitable for 5 to 7.5 HP Motor inclusive of taxes | each | 1
|  | Labour charges for removing the existing unserviceable bearing and fixing the new ball bearing with special T&P. (on cost of Ball Bearing) |  | 50%
Transportation and Rounding off
Rate per Each
| 18.2.5 | Replacing the existing bearing of approved make for electric motor single phase / 3 phase AC upto 15 to 20 HP of all types with due alignment of the shaft and tested.
a) Material
|  | Ball Bearings suitable for 5 to 7.5 HP Motor inclusive of taxes | each | 1
|  | Labour charges for removing the existing unserviceable bearing and fixing the new ball bearing with special T&P. (on cost of Ball Bearing) |  | 50%
Transportation and Rounding off
Rate per Each
| 18.2.6 | Replacing the ball bearing of table / cabin / pedestal / ceiling / exhaust fan complete with alignment of shaft and tested.
a) Material
|  | Ball Bearings suitable for table / cabin / ceiling / Exhaust Fan inclusive of taxes | each | 1
|  | Labour charges for removing the existing unserviceable bearing and fixing the new ball bearing with special T&P. (on cost of Ball Bearing) |  | 50%
Transportation and Rounding off
Rate per Each
| 18.2.7 | Replacing the ball bearing of bush / rubber / ring washers for fan mortar complete with alignment of shaft and tested.
a) Material
|  | Cost of GM / Bush / Rubber / Ring washer etc., | each | 1
|  | Labour charges for removing the existing unserviceable bush/ ring washer and fixing the new with special T&P.(on cost of material) |  | 50%
Rounding Off
Rate per Each
| 18.2.8 | Replacing the existing capacitor of table / cabin / pedestal / ceiling / exhaust fan complete with wiring.
a) Material
|  | Cost of 2.5 / 3.5 mfd condensor suitable for ceiling / pedastal Exhaust Fan | each | 1
b) Labour charges for removing and refixing
|  | Semi Skilled Electrician | day | 0.1
Rounding Off
Rate per Each
Note : Labour considered for 10 jobs / day
31-10-2006

## Bus Bars
12 | BUS BARS
12.1 | Copper Bus Bars
12.1.1 | Supply and fabrication and erection of following sizes of 4Nos of copper bus bars in the existing sheet steel enclosure with resin cast insulator supports etc., complete including cost and conveyance of all materials all labour charges.
D.No. | Size of each bar in mm | No.of 1 mtr bars | Current rating in each bar | Weight / mtr in Kg | Rate per Kg | Cost of copper bars | Cost of 8Nos. Resin cast insulator. @ Rs.35/- Each | Labour charges for fabrication and fixing of insulators providing with PVC heat shrinkable sleeves. | Total Amount mtr | Rounding off
a | 20x3 | 4 Nos | 220A | 0.529 Kg
b | 20x6 | 4 Nos | 300A | 1.072
c | 25x3 | 4 Nos | 270A | 0.663
d | 25x6 | 4 Nos | 350A | 1.34
e | 30x6 | 4 Nos | 400A | 1.608
f | 40x6 | 4 Nos | 520A | 2.144
g | 50x6 | 4 Nos | 630A | 2.68
h | 60x6 | 4 Nos | 760A | 3.216
i | 75x6 | 4 Nos | 970A | 4.02
j | 100x6 | 4 Nos | 1380A | 5.36
Note : Labour Charges @ 20 % on Copper cost is allowed
12.2 | Aluminum Bus Bars
12.2.1 | Supply and fabrication and erection of following sizes of 4Nos of aluminum bus bars in the existing sheet steel enclosure with resin cast insulator supports etc., complete including cost and conveyance of all materials all labour charges.
D.No. | Size of each bar in mm | No.of 1 mtr bars | Current rating in each bar | Weight / mtr in Kg | Rate per Kg | Cost of copper bars | Cost of 8Nos. Resin cast insulator. @ Rs.35/- Each | Labour charges for fabrication and fixing of insulators providing with PVC heat shrinkable sleeves. | Total Amount mtr | Rounding off
a | 20x3 | 4 Nos | 145A | 0.161 Kg
b | 20x6 | 4 Nos | 195A | 0.322
c | 25x3 | 4 Nos | 180A | 0.201
d | 25x6 | 4 Nos | 230A | 0.402
e | 40x6 | 4 Nos | 350A | 0.644
f | 50x6 | 4 Nos | 425A | 0.805
g | 60x6 | 4 Nos | 500A | 0.966
h | 75x6 | 4 Nos | 680A | 1.207
j | 100x6 | 4 Nos | 900A | 1.61
Note : Labour charges are as per the rates allowed for Copper bus bar since, there is no difference in the requirement of Labour

## Temporary Illumination
DATA ANALYSIS FOR TEMPORARY ILLUMINATION
Data No. | Description | Capital Cost | Life in days | Depreciation: Capital cost /Life in days | Maintenance 50% of depreciation | Interest @ 12% on Capital cost/days in a year | Labour charges | Storage charges @ 1% on capital cost/No.of days in a year | Transportation charges @ 2% on capital cost/No.of days in a year | Hire charges per day
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
16 | TEMPORARY ILLUMINATION
16.1 | Hire charges for Temporary illumination, consisting of 6.2 strip lights (navar patta) complete with 1000 Nos required wire leads duly erected and dismantled without scaffolding including cost and conveyance of all materials and labour charges etc., complete for one day. | 1000 Nos bulbs & 30 Mtrs 7/20 service wire | 1 year i.e 60 days |  |  |  | 1.Skill electrician 1.Helper
16.2 | Hire charges for Temporary illumination, consisting of 6.2 strip lights (navar patta) complete with 1000 Nos required wire leads duly erected and dismantled with scaffolding including cost and conveyance of all materials and labour charges etc., complete for one day. | 1000 Nos bulbs & 30 Mtrs 7/20 service wire | 1 year i.e 60 days |  |  |  | 1.Skill electrician 1.1Helper
16.3 | Hire charges for Temporary illumination, consisting of tube light with patti type 4'-40W complete with required wire leads duly erected and dismantled without scaffolding including cost and conveyance of all materials and labour charges etc., complete for one day. | 1 No tube light, 4 Mtrs 7/20 service wire | 3years i.e 3 x 60 = 180 days |  |  |  | 0.06 Skill electrician 0.06Helper
16.4 | Hire charges for Temporary illumination, consisting of tube light with patti type 4'-40W complete with required wire leads duly erected and dismantled with scaffolding including cost and conveyance of all materials and labour charges etc., complete for one day. | 1 No tube light, 4 Mtrs 7/20 service wire | 3years i.e 3 x 60 = 180 days |  |  |  | 0.06 Skill electrician 0.10Helper
16.5 a | Hire charges for Temporary illumination, consisting of flood light 1000W hallogen with lamp complete with required wire leads duly erected and dismantled without scaffolding including cost and conveyance of all materials and labour charges etc., complete for one day. | 1 No 1000W Halogen, 30 Mtrs 7/20 service wire | 3years i.e 3 x 60 = 180 days |  |  |  | 0.25 Skill electrician 0.25Helper
16.5 b | Hire charges for Temporary illumination, consisting of flood light 500W hallogen with lamp complete with required wire leads duly erected and dismantled without scaffolding including cost and conveyance of all materials and labour charges etc., complete for one day. | 1 No 500W Halogen, 30 Mtrs 7/20 service wire | 3years i.e 3 x 60 = 180 days |  |  |  | 0.25 Skill electrician 0.25Helper
16.5 c | Hire charges for Temporary illumination, consisting of flood light 250W metal halide fitting with lamp complete with required wire leads duly erected and dismantled without scaffolding including cost and conveyance of all materials and labour charges etc., complete for one day. | 1 No 250W Metal halide, 30 Mtrs 7/20 service wire | 3years i.e 3 x 60 = 180 days |  |  |  | 0.25 Skill electrician 0.25Helper
16.5 5 | Hire charges for Temporary illumination, consisting of flood light 400W metal halide fitting with lamp complete with required wire leads duly erected and dismantled without scaffolding including cost and conveyance of all materials and labour charges etc., complete for one day. | 1 No 400W Metal halide, 30 Mtrs 7/20 service wire | 3years i.e 3 x 60 = 180 days |  |  |  | 0.25 Skill electrician 0.25Helper
16.6 a | Hire charges for Temporary illumination, consisting of flood light 1000W hallogen with lamp complete with required wire leads duly erected and dismantled with scaffolding including cost and conveyance of all materials and labour charges etc., complete for one day. | 1 No 1000W Halogen, 30 Mtrs 7/20 service wire | 3years i.e 3 x 60 = 180 days |  |  |  | 0.25 Skill electrician 0.30Helper
16.6 b | Hire charges for Temporary illumination, consisting of flood light 500W hallogen with lamp complete with required wire leads duly erected and dismantled with scaffolding including cost and conveyance of all materials and labour charges etc., complete for one day. | 1 No 500W Halogen, 30 Mtrs 7/20 service wire | 3years i.e 3 x 60 = 180 days |  |  |  | 0.25 Skill electrician 0.30Helper
16.6 c | Hire charges for Temporary illumination, consisting of flood light 250W metal halide fitting with lamp complete with required wire leads duly erected and dismantled with scaffolding including cost and conveyance of all materials and labour charges etc., complete for one day. | 1 No 250W Metal halide, 30 Mtrs 7/20 service wire | 3years i.e 3 x 60 = 180 days |  |  |  | 0.25 Skill electrician 0.30Helper
16.6 d | Hire charges for Temporary illumination, consisting of flood light 400W metal halide fitting with lamp complete with required wire leads duly erected and dismantled with scaffolding including cost and conveyance of all materials and labour charges etc., complete for one day. | 1 No 400W Metal halide, 30 Mtrs 7/20 service wire | 3years i.e 3 x 60 = 180 days |  |  |  | 0.25 Skill electrician 0.30 Helper
16.7 | Hire charges for Temporary illumination, consisting of white / colour series light 6.2v complete with 1000 Nos. with required wire leads duly erected and dismantled without scaffolding including cost and conveyance of all materials and labour charges etc., complete for one day. | 1000 Nos bulbs & 30 Mtrs 7/20 service wire | 1 year i.e 60 days |  |  |  | 0.5 Skill electrician 0.5Helper
16.8 | Hire charges for Temporary illumination, consisting of white / colour series light 6.2v complete with 1000 Nos. with required wire leads duly erected and dismantled with scaffolding including cost and conveyance of all materials and labour charges etc., complete for one day. | 1000 Nos bulbs & 30 Mtrs 7/20 service wire | 1 year i.e 60 days |  |  |  | 0.5 Skill electrician 1.0 Helper
16.9 | Hire charges for Providing and fixing rotating machine to give running effect to strip lights and miniature lights upto a load of 10KW with required wire leads duly dismantled including cost and conveyance of all materials and labour charges etc., complete for one day. | Cost of 10 KW rotating machine | 5 years i.e 5 x 30 = 150 days |  |  |  | 0.25 Helper
16.1 | Hire charges for Providing oscillating type pedestal fan 16" / 18" with connected wire leads duly dismantled including cost and conveyance of all materials and labour charges etc., complete for one day. | 18" pedestal fan, 30 Mtrs 7/20 service wire | 3years i.e 3 x 40 = 120 days |  |  |  | 0.10 Helper
16.11 | Hire charges for Providing air cooler connected with necessary mains switch gear with continues earth lead during function duly dismantled including cost and conveyance of all materials and labour charges etc., complete for one day. | Air cooler, 30 Mtrs 7/20 service wire | 3years i.e 3 x 40 = 120 days |  |  |  | 0.20 semi-skilled electrician
16.12 | Hire charges for Providing 1.5 ton/2.0 ton capacity window air conditioning unit complete with suitable stabilizer with temporary frame and fabrication work and required materials achieve cooling, temperature connected with necessary mains switch gear with continues earth lead during function duly dismantled including cost and conveyance of all materials and labour charges etc., complete for one day. | Air conditioned, stabilizer | 8years i.e. 8 x 15 = 120 days |  |  |  | 1 skilled electrician, 2 Helpers, 1 carpenter
16.13 | Hire charges for Providing temporary plug point with 5 pin 6 Amps/16 Amps with necessary mains switch gear with continues earth lead during function duly dismantled including cost and conveyance of all materials and labour charges etc., complete for one day. | 16 Amps 5 in one power plug, 30 Mtrs 7/20 service wire | 3years i.e 3 x 40 = 120 days |  |  |  | 0.05 semi-skilled electrician
Note : 1) The rates are for one glowing/working day.
2) Allow 50% of rate for each day upto 3 days (i.e. 2nd and 3rd day)
3) For each additional day after 3 days, but not exceeding 15 days, allow 25 % rate of glowing/working days
4) For more than 15 days allow 10% per day but total rental charges shall not exceeded 80% of capital cost of item.
16.14 a | Hire charges for supply and maintaining 125 KVA, 415 voltage, 50 C/s AC generating set with all standard accessories such as control panel, batteries etc complete for one day excluding cost of fuel. | 125 KVA DG Set, 200 Amps main switch | 10years i.e 10 x 60 = 600 days |  |  |  | 1.Skill Electrician
16.14 b | Hire charges for supply and maintaining 82.5 KVA, 415 voltage, 50 C/s AC generating set with all standard accessories such as control panel, batteries etc complete for one day excluding cost of fuel. | 82.5 KVA DG Set, 200 Amps main switch | 10years i.e 10 x 60 = 600 days |  |  |  | 1.Skill Electrician,
16.14 c | Hire charges for supply and maintaining 62.5 KVA, 415 voltage, 50 C/s AC generating set with all standard accessories such as control panel, batteries etc complete for one day excluding cost of fuel. | 62.5 KVA DG Set, 200 Amps main switch | 10years i.e 10 x 60 = 600 days |  |  |  | 1.Skill Electrician,
16.14 d | Hire charges for supply and maintaining 30 KVA, 415 voltage, 50 C/s AC generating set with all standard accessories such as control panel, batteries etc complete for one day excluding cost of fuel. | 30 KVA DG Set, 100 Amps main switch | 10years i.e 10 x 60 = 600 days |  |  |  | 1.Skill Electrician,
16.14 e | Hire charges for supply and maintaining 5 to 15 KVA, 415 voltage, 50 C/s AC generating set with all standard accessories such as control panel, batteries etc complete for one day excluding cost of fuel. | 5 to 15 KVA DG Set, 63 Amps main switch | 10years i.e 10 x 60 = 600 days |  |  |  | 1.Skill Electrician,
16.15 | Hire charges for supply and maintaining of 125 KVA DG set with acoustic enclosure as per IS specification with DCM 4 wheeler vehicle with all standard accessories such as control panel, batteries etc complete for one day excluding cost of fuel. | 125 KVA DG Set, acoustic enclosure, 200 Amps main switch with 4 wheeler DCM vehicle. | 10years i.e 10 x 60 = 600 days |  |  |  | 1.Skill Electrician,
NOTE: 1) The above rates are applicable per one day only.
2) For subsequent days the above rte shall be reduced by 25% after 8th day reduce the rate by 50%
3) Diesel cost will be paid extra for running hours at the prevailing rates.
4) For test run,. The minimum req2uirement of the fuel shall be born by the contractor.
5) The D.G.set should be in good condition and the life of set shall not b e beyond 10 years
16.16 a | Hire charges for supply and maintaining towards supply and run of 2 of 2.5 sq mm to 6 sq mm VIR/WPTC/WPSC cable with necessary terminations etc., complete for one day. | 2 of 6 sq mm WPTC cable 1 mtr | 3years i.e 3 x 60 = 180 days |  |  |  | 0.015 Helper
16.16 b | Hire charges for supply and maintaining towards supply and run of 2 of 10 sq mm VIR/WPTC/WPSC cable with necessary terminations etc., complete for one day. | 2 of 10 sq mm WPTC cable 1 mtr | 3years i.e 3 x 60 = 180 days |  |  |  | 0.02 Helper
16.16 c | Hire charges for supply and maintaining towards supply and run of 35 sq mm x 3 1/2 core UG cable with necessary terminations etc., complete for one day. | 35 sq mm x 3 1/2 UG cable 1 mtr | 3years i.e 3 x 60 = 180 days |  |  |  | 0.05 Helper
16.16 d | Hire charges for supply and maintaining towards supply and run of 50 sq mm x 3 1/2 core UG cable with necessary terminations etc., complete for one day. | 50 sq mm x 3 1/2 UG cable 1 mtr | 3years i.e 3 x 60 = 180 days |  |  |  | 0.05 Helper
16.16 e | Hire charges for supply and maintaining towards supply and run of 95 sq mm x 3 1/2 core UG cable with necessary terminations etc., complete for one day. | 95 sq mm x 3 1/2 UG cable 1 mtr | 3years i.e 3 x 60 = 180 days |  |  |  | 0.05 Helper
16.16 f | Hire charges for supply and maintaining towards supply and run of 120 sq mm x 3 1/2 core UG cable with necessary terminations etc., complete for one day. | 120 sq mm x 3 1/2 UG cable 1 mtr | 3years i.e 3 x 60 = 180 days |  |  |  | 0.05 Helper
16.16 g | Hire charges for supply and maintaining towards supply and run of 185 sq mm x 3 1/2 core UG cable with necessary terminations etc., complete for one day. | 185 sq mm x 3 1/2 UG cable 1 mtr | 3years i.e 3 x 60 = 180 days |  |  |  | 0.05 Helper
16.17 | Hire charges for providing industrial type panel board consisting of bus bar chamber with 200/250 amps incoming TP/MCCB as incomers switch, 12 nos 100 amps fuse unit, earth wire erected and dismantled all accessories etc., complete for distribution for one day. | 250 Amps bus bar, 250 TPN/MCCB, 12 nos 100 Amps fuse units | 10years i.e 10 x 15 = 150 days |  |  |  | 0.5 Skilled electrician, 1 Helper
16.18 a | Hire charges for supply and maintaining towards supply and fixing of 100 amps 4 pole change over switch/TPN switches including erection and dismantled all accessories etc., complete for one day. | 100 Amps COS/ TPN | 10years i.e 10 x 15 = 150 days |  |  |  | 0.125 Skilled electrician, 0.125 Helper
16.18 b | Hire charges for supply and maintaining towards supply and fixing of 200 amps 4 pole change over switch/TPN switches including erection and dismantled all accessories etc., complete for one day. | 200 Amps COS/ TPN | 10years i.e 10 x 15 = 150 days |  |  |  | 0.125 Skilled electrician, 0.125 Helper
16.18 c | Hire charges for supply and maintaining towards supply and fixing of 400 amps 4 pole change over switch/TPN switches including erection and dismantled all accessories etc., complete for one day. | 400 Amps COS/ TPN | 10years i.e 10 x 15 = 150 days |  |  |  | 0.2 Skilled electrician, 0.2 Helper
16.19 a | Hire charges for supply and erection and dismantle of 4 pole structure of 4 of 20' GI pipe of 50/80mm structure complete necessary cross arms and hardware materials for fixing halogen/ metal halide fitting with suitable earthing arrangements including cost conveyance of all materials and labour charges for maintaining one day. | 24 Mtrs 80/ 50mm C class GI pipe, 50/50 MS cross arms weight of 72 Kgs & 1 No. coil earthing | 15years i.e 15 x 12 = 180 days |  |  |  | 0.5 fitter, 0.5 skilled electrician, 2 Helpers, 54 Cum.
16.19 b | Hire charges for supply and erection and dismantle of 4 pole structure of 4 of 30' GI pipe of 50/80mm structure complete necessary cross arms and hardware materials for fixing halogen/ metal halide fitting with suitable earthing arrangements including cost conveyance of all materials and labour charges for maintaining one day. | 36 Mtrs 80/50mm C class GI pipe, 50/50 MS cross arms weight of 72 Kgs & 1 No.coil earthing | 15years i.e 15 x 12 = 180 days |  |  |  | 0.5 fitter, 0.5 skilled electrician, 2 Helpers, 54 Cum.
NOTE: 1) The rates are for one glowing/working day.
2) Allow 50% of rate for each day upto 3 days (i.e. 2nd and 3rd day)
3) For each additional day after 3 days, but not exceeding 15 days, allow 25 % rate of glowing/working days
4) For more than 15 days allow 10% per day but total rental charges shall not exceeded 80% of capital cost of item.
Note : Service Tax and VAT as applicable shall be extra for all Items.